SCK CEN Ref.: SCK CEN/90508872

Addendum II -  Cryoplant Technical Requirements

Technical Specifications and Project Requirement

Tender reference: 2024-106-IVE

© SCK CEN - Stichting van Openbaar Nut – Fondation d'Utilité Publique ‐ Foundation of Public Utility
Registered Office: Avenue Herrmann Debroux 40 – BE‐1160 BRUSSEL
Research Centres:

Boeretang 200 - 2400 MOL – Belgium

Chemin du Cyclotron 6 - 1348 Ottignies-Louvain-la-Neuve – Belgium

www.sckcen.be

Copyright Rules

All property rights and copyright are reserved to SCK CEN.  In case of a contractual arrangement with SCK CEN, the use of this information by a Third Party, or for any purpose other than for which it is intended based on the contract, is not authorized.  With respect to any unauthorized use, SCK CEN makes no representation or warranty, expressed or implied, and assumes no liability as to the completeness, accuracy or usefulness of the information contained in this document, or that its use may not infringe privately owned rights.

Table of Contents

I.1	Abbreviations	5

I.2	Terms and Definitions	6

I.3	Table of Figures	9

I.4	Table of Tables	10

1	Introduction	12

1.1	The LINAC	12

1.2	Cryogenic System	12

1.3	Cryogenic Users	13

1.4	Overview of the He lines	14

1.5	Introduction to QPLANT Control & Interlock System, CIS services and infrastructure.	16

2	Nature of the Procurement	17

2.1	Scope of Work by the Contractor	17

2.2	Scope of Supply by the Contractor	17

3	Technical Requirements	18

3.1	Introduction	18

3.2	Nominal Operational Scenarios	19

3.2.1	Lifetime and annual maintenance schedule	19

3.2.2	Steady state operational scenarios	19

3.2.3	Transient operational scenarios	19

3.2.4	Other operational scenarios	21

3.3	Performance Requirements	22

3.4	Reliability Requirements	23

3.5	Reliability Centred Maintenance & Lifecycle Cost Management	23

3.6	QPLANT Design & Build Requirements	24

3.6.1	Units	24

3.6.2	3D Model	24

3.6.3	Energy-efficiency	25

3.6.4	Helium Inventory Management	25

3.6.5	Warm Storage Helium	27

3.6.6	Warm Compressor Station	29

3.6.7	Refrigeration Cold Box	33

3.6.8	Purging	37

3.6.9	Design, Materials	37

3.6.10	Welding	41

3.6.11	Machine Protection	42

3.6.12	General Electrical Requirements	42

3.7	QPLANT Control System	43

3.7.1	Overview	43

3.7.2	Reference Architecture	44

3.7.3	Architecture, Autonomy, and Scope	44

3.7.4	Network	45

3.7.5	Software Change Management	47

3.7.6	Test System for Functional Verification	48

3.7.7	Digital Process Model	48

3.7.8	Cryogenic System Control and MCS Integration	49

3.7.9	General Software and Hardware Requirements	49

3.7.10	Software development	49

3.7.11	Human Machine Interface (HMI)	50

3.7.12	Migration to Newer Hardware	51

3.8	Interfaces	52

3.8.1	Process Line interface	52

3.8.2	Interface with support systems (utilities)	55

3.8.3	Interfaces with the site	58

Figure 2	58

3.8.4	Interfaces with the Vacuum System	59

3.8.5	Interface with LHe (ad-hoc) user and associated helium recovery	59

3.8.6	Liquid Nitrogen (LN2)	61

3.8.7	Interfaces with (external) Control System	62

3.9	Quality assurance during design and build	63

3.9.1	Manufacturing and Inspection Plan	63

3.9.2	Pressure, and leak tests	64

3.9.3	Electrical, wiring and control system tests	64

3.9.4	Tests of components	64

3.9.5	Packaging, Transport and Storage	64

3.10	Incoming Inspection at SCK CEN Site	65

3.11	Installation	65

3.11.1	Quality Assurance After Mechanical Assembly	65

3.12	Standalone Commissioning	66

3.12.1	Tests to be done during Standalone Commissioning	67

3.13	Acceptance Testing	67

3.13.1	General Requirements	67

3.13.2	Factory Acceptance Test (FAT)	69

3.13.3	Site Acceptance Tests (SAT)	69

3.14	Spare Parts	71

3.15	After-sales Services	72

3.15.1	Level Agreement (Option 3)	72

3.15.2	Lifetime After-sales Services (applicable when Option 3 is exercised)	72

3.16	Documentation and Deliverables (DD-#)	73

3.16.1	OEM Documentation	75

4	Safety, Codes and Standards	76

4.1	Safety	76

4.1.1	Hazard definitions and typical mitigation devices	76

4.1.2	ODH Monitoring Architecture and Responsibilities	76

4.2	Codes and Standards	78

4.2.1	Electromagnetic interference	79

4.2.2	Pressure Equipment & Safety	79

4.2.3	Functional Safety & Control	79

4.2.4	Asset & Maintenance Management	80

4.2.5	Cleanliness & Purity	80

4.2.6	Proof-Test & Control-Phase Requirements	80

5	Schedule	81

5.1	Contractual Phases	81

5.2	Preliminary Schedule	82

5.3	Hold and Witness Points	83

6	Contract Performance	84

6.1	General Organization	84

6.2	Communication	84

6.3	Contract Management	84

6.3.1	Progress Dashboard	84

6.3.2	Meetings	85

6.4	Risk Assessment and Risk Management Plan	86

6.5	Factory Access	86

7	Quality Assurance and Control	87

7.1	Quality Assurance	87

7.1.1	General requirements	87

7.1.2	Quality Management System	87

7.1.3	Quality Assurance Program	87

7.1.4	Qualification of personnel	87

7.1.5	Document Retention and Submission Requirements	87

7.1.6	Change Management	88

7.1.7	Non-Conformity Management	88

7.1.8	Audits	89

7.2	Quality Control	90

7.2.1	General requirements	90

7.2.2	Declaration of conformity with all requirements	90

7.3	Acceptance and Warranty	90

7.4	Final acceptance	91

8	Appendix	93

8.1	Cooling Power for Cool-down	93

8.1.1	Simplified cooling model	93

8.1.2	System Mass Summary	93

8.1.3	Static heat load as a function of temperature	94

8.1.4	Enthalpy data of metal at various temperatures	94

8.2	Control Systems	95

8.2.1	Instructions for GQRC	95

8.2.2	Control Architecture details	96

9	Applicable Documents	99

## Abbreviations

| ACC NF | Accelerator Nuclear Facilities (buildings and utilities) |
| --- | --- |
| AD | Applicable Documents |
| AH | Atmospheric Heat exchanger |
| BSL | Baseline |
| CAV | Cavity |
| CCB | Cryogenic Compressor Building |
| CEA | French Alternative Energies and Atomic Energy Commission |
| CIS | Control and Interlock system |
| COTS | Commercial Off-The-Shelf, see also OEM |
| CSS | Cryogenic Supply System (QPLANT+QINFRA+QDIST) |
| CV | Control Valve |
| DD | Documentation Deliverables |
| DIS | Device Interlock System (part of MIS) |
| DSBT | Low Temperature Systems Department |
| EH | Electrical Heater |
| FAT | Factory Acceptance Test |
| FMECA | Failure mode, effects, and criticality analysis |
| FT | Fault Tolerance |
| GHe | Gaseous Helium |
| HAZOP | HAZard and OPerability |
| He | Helium |
| HMI | Human Machine Interface |
| HIM | Helium Inventory Management System |
| HP | High Pressure (typically 15 bar for WCS-HP) |
| HVAC | Heating, Ventilation and Air Conditioning |
| HV | Hand Valve |
| HX | Heat Exchanger |
| KOM | Kick-Off Meeting |
| LHe | Liquid Helium |
| LINAC | Linear Accelerator |
| LN2 | Liquid Nitrogen |
| LP | Low Pressure (Typically 1050 mbar) |
| LRU | Line Replaceable Unit (used with RCM and MTBF data) |
| LTU | LINAC Tunnel |
| LWC | Low Pressure Warm Compressor |
| MCS | Control System |
| MIP | Manufacturing and Inspection Plan |
| MIS | Interlocking System |
| MIT | IT System |
| MTBF | Mean Time Between Failure |
| MTBM | Mean Time Between Maintenance |
| MTTR | Mean Time To Repair |
| MYRRHA | Multi-purpose hYbrid Research Reactor for High-tech Applications |
| OEM | Original Equipment Manufacturer. (e.g. Kaeser) |
| ORS | Oil removal system |
| PEPS | Personal Protection System |
| PFD | Process Flow Diagram |
| PID | Piping and Instrumentation Diagram |
| PLC | Programmable Logic Controller |
| QCELL | Cryogenic Cell = QVB+QM |
| QLM | Main Cryogenic Distribution Line |
| QM | Cryomodule |
| QPLANT | QPLANT |
| QPLANT:CIS | QPLANT Control and Interlock System |
| QRB | QPLANT Refrigeration Cold Box |
| QSYS | Cryogenic System |
| QSYS:CS | Cryogenic Control System |
| QVB | Cryogenic Valve Box |
| QVE | End-box |
| RAMI | Reliability, Availability, Maintainability, Inspectability. |
| RF | Radio Frequency |
| SAT | Site Acceptance Test |
| SC | Superconducting |
| SHe | Supercritical Helium |
| SSC | Structures Systems and Components |
| ST | Storage |
| SV | Safety Valve |
| TRO | Technical Responsible Officer |
| TRM | Technical Review Meeting |
| TS | Thermal Shields |
| Tu | Turbo Expander |
| UPS | Uninterruptible Power Supply |
| VLP | Very Low Pressure (Typically 27-31 mbar for QRB-B and ~400-450 mbar for WCS-VLP) |
| WCS | Warm Compressor Station |
| WSH | Warm Storage Helium |

## Terms and Definitions

| Conceptual Process Proposal | A preliminary engineering framework that defines the cryogenic helium refrigeration architecture, supporting a range of operational and functional requirements. The Conceptual Process Proposal serves as the foundation for subsequent design stages by detailing the system architecture, proposed configurations, and functional decompositions necessary to meet the overarching System Requirements. It ensures integration of key subsystems and process units while maintaining compliance with operational constraints, safety margins, and performance criteria. It is reviewed and validated as a baseline for the Detailed Design phases |
| --- | --- |
| CoreShare | SCK CEN’s document management system |
| (Inverse) Coefficient of Performance | COP: A dimensionless indicator of the energy efficiency of refrigeration, representing the ratio of useful thermal energy delivered to the electrical energy consumed. In cryogenic applications, COP refers specifically to the amount of cooling power generated at cryogenic temperatures per unit of electrical input. Defined as: COP_cryogenic = Q_cooling / P_input where: Q_cooling = Net cooling power at cryogenic temperature [W] P_input = Total input power. Inverse Coefficient of Performance (invCOP): A measure of specific power consumption in refrigeration systems, defined as the amount of input electrical energy required to produce one unit of cooling at the specified cryogenic temperature. Commonly expressed in W/W (e.g., W per W of cooling at 4.5 K). Lower values indicate higher efficiency. Defined as: invCOP_cryogenic = P_input / Q_cooling = 1 / COP_cryogenic |
| Design Stage(s) / Project Execution Stages | A self-contained phase within the engineering design process, each focusing on a distinct level of technical maturity and output deliverables. Design Stages are sequenced to transform user requirements into realizable system configurations through increasing levels of fidelity and validation. Conceptual Design Phase: A phase in the design process that involves evaluating multiple concepts to determine their ability to fulfil the defined fit-for-purpose requirements. It includes the identification and justification of a reference concept deemed the most suitable and feasible within the specified constraints. The Conceptual Design provides a general understanding of the system's intended purpose, overall structure, operating principles, physical dimensions, and key technical specifications. Once reviewed and approved, the Conceptual Design serves as the foundation for the development of the Detailed Design. Detailed Design Phase: This stage develops the finalized and exhaustive Design Documentation required for fabrication, inspection, testing, installation, commissioning, operation, maintenance, refurbishment, and decommissioning of the System. Documentation must meet quality, regulatory, and lifecycle expectations.. |
| Digital Process Model | The software model (transient or steady state) representing cryogenic behaviour; may form part of or interface with the Test System. |
| Digital Twin | A full scope, continuously synchronized digital representation of the QPLANT; not mandatory. |
| Functional Test Plan (FTP) | A structured, traceable document defining functional verification for each System Under Test (SUT) and its Control and Interlock System (SUT:CIS). It shall specify test cases, inputs, interfaces, control sequences, monitoring logic, and acceptance criteria to demonstrate compliance with the stated requirements |
| Hold Point | A mandatory verification point beyond which work cannot continue without approval by SCK CEN. The work can only continue provided that SCK CEN has been able to verify the quality of the work completed so far and has confirmed its approval of such work in writing. |
| Life Cycle Phase | Predefined execution stages with a staged gate and milestone. L1: Conceptual Design L2: Detailed Design L3: Build (Construction, Assembly) L4: Installation L5: Commissioning L6: Acceptance Testing Lifecycle Phases related to specific documentation (deliverables) and verification and validation activies |
| Lifecycle Cost Management | The cost optimization approach used during the post-commissioning phase to manage preventive maintenance, replacement strategy, and reliability targets. It is supported by failure forecasting, risk-based planning, and system performance modelling to maintain or reduce lifetime cost without compromising function. |
| LOOP event | Loss Of Offsite Power is event characterized by the loss of external electrical supply to the QPLANT. |
| Maximum Allowable Pressure | It is defined in PED (2014/68/EU) as the maximum pressure for which equipment is designed. |
| Noise Measurement | Noise Measurement (general). Unless stated otherwise, all sound levels are A-weighted and expressed in dB(A), measured at 1 m from the equipment envelope at approximately 1.5 m microphone height, under free-field over a reflecting plane conditions, using a Class 1 sound level meter (IEC 61672). Background noise shall be at least 10 dB below measured levels or corrected per the test standard. “Compressor (unit)” means an individual compressor with its motor/drive. “Complete skid” means the full assembly with all compressors and drives operating. |
| Operating Pressure | Expected maximum pressure (including safety relief from passive or active systems) in any operational scenario, including startup, shutdown, or transient conditions. |
| Reliability Centred Maintenance | A systematic and structured process to determine the most effective maintenance approach for an asset or system. RCM seeks to ensure that systems continue to do what their users require in their current operating context. It involves identifying failure modes, assessing their consequences, and selecting initiative-taking maintenance tasks to mitigate risk while optimizing cost, safety, and system availability. |
| Risk Register | A formal tool used to systematically document, track, and manage risks throughout a project, with the primary purposes of risk identification, assessment, treatment, monitoring, and communication. |
| Set Pressure | Defined in API 520 as the pressure at which safety valves are set to open (typically ≥10 % above Operating Pressure). |
| Shut-off Valve | A shut-off valve is a valve that is automatically actuated (e.g., electrically, pneumatically, or hydraulically) and triggered by a process or safety interlock event. It is intended to isolate helium flow in response to defined conditions such as emergency shutdown, overpressure, or equipment trip. It differs from a manual isolation valve, which is operated only by human intervention. Shut-off valves are designed to fail-safe and to maintain full functionality across repeated cycles between ambient and cryogenic conditions. |
| System Under Test (SUT) | The actual system being verified (e.g. QPLANT or QPLANT:CIS) |
| Test System | The digital and/or physical platform used to validate the SUT during commissioning; it replicates control logic, I/O response, and process dynamics and may include a digital process model (transient simulation or digital twin). |
| Terminal Point | A physical interface with SCK CEN infrastructure, specifically ACC NF. |
| Validation | Ensures that the right product is built, confirming that the system meets the needs and expectations of the end-users or stakeholders. Occur after verification processes, typically at the end of a development phase or project. Validation involves evaluating the final product to ensure it meets the needs of the intended end-user or customer. |
| Verification | Confirms that the product is built correctly according to the specified requirements, ensuring compliance with regulations and specifications. Conducted throughout the development lifecycle, including during production or development phases. These activities involve reviews, inspections, and testing to ensure compliance with specifications. |
| Warm Compressor Station | Composed of LP to HP and VLP to LP compressors, the Oil Removal System, the gas management panel, and the necessary electrical cabinets. |
| Witness Point | A point in the process where SCK CEN will verify the quality of the work completed. However, the work may continue meanwhile. |

## Table of Figures

Figure 1 Overall layout of the Cryogenic System	12

Figure 2 View of the buildings related to the QPLANT.	13

Figure 3 Simplified interface diagram of the QPLANT depicting a single representative ‘QCELL’ (inside grey dotted line) as a proxy for all heat load sources.  Temperatures shown are indicative of the 2 K operating scenario.	14

Figure 4 QPLANT’s simplified Process Flow Diagram	15

Figure 5 QPLANT - Control and Interlock related systems	16

Figure 6 Operational scenarios and transitions for the Cryogenic System.  Blue boxes indicate steady states while light blue boxes indicate transients	20

Figure 7 Direct Drive	30

Figure 8 WSH with Contingent Part 2 (area covered in purple dotted line)	27

Figure 9  Reference Architecture of the Cryogenic Control System	44

Figure 10 Software Change Management	47

Figure 11 MIT Reference Architecture	45

Figure 12 Preliminary arrangement of the pipes in the QLM -  see Table 12 for details	53

Figure 13 Routing of QRB.EUR (External User Recovery)	61

Figure 14 Simplified cooling model	93

## Table of Tables

Table 1 Main interfacing and helium transport lines	14

Table 2 Operational Scenarios	19

Table 3 Heat Loads Summary from QCELLs and Cryogenic Distribution	22

Table 4 Fluid Conditions at the Refrigerator Cold Box Interfaces for Different Operating Scenarios	23

Table 5 Temperature measurement precision	40

Table 6 He Leakage requirements (excluding via permeation and diffusivity)	25

Table 7 Helium Inventory	26

Table 8 Measuring Points for WCS	33

Table 9 Measuring Points for QRB	37

Table 10 Measuring points for gas helium storages.	28

Table 11  Interface ID between QRB and QDIST  (cold interfaces)	53

Table 12 Preliminary pipe diameters for the QLM	54

Table 13  Interface ID between QRB and QINFRA  (warm interfaces)	54

Table 14 Internal QPLANT Distribution Lines (crossing multiple rooms)	54

Table 15 Warm lines at room temperature	55

Table 16 External Helium User Quantification	60

Table 17 Project Lifecycle Phases.	81

Table 18 Documentation and Deliverables	74

Table 19 Pressure Equipment and Safety Standards	79

Table 20 Functional Safety & Control Standards	79

Table 21 Asset & Maintenance Management	80

Table 22 Cleanliness And Purity	80

Table 23 Preliminary Schedule and Main Milestones	82

Table 24 System mass	93

Table 25 Weighted Average Enthalpy Data (1K - 300K)	94

Table 26 Instructions for GSHRC	95

Table 27 Control Architecture details	96

Table 28 Applicable Documents (AD)	99

Introduction

“Phase 1 – Implementation” of the MYRRHA program focuses on the design, construction, and commissioning of a 4 mA 100 MeV super-conducting CW proton Linear Accelerator (LINAC), a Proton Target Facility (PTF) and a Full Power Facility (FPF).  (Phase 2 of the MYRRHA program will be the extension to 600 MeV).  Further information about MYRRHA Phase I is provided in reference [AD 1].

The LINAC

The ~160 m long LINAC consists of a normal conducting injector followed by a superconducting section.  The latter section accelerates protons from 17 to 100 MeV using 352.2 MHz single-spoke cavities operating at 2 K.  Each Cavity (CAV) is submerged in saturated superfluid helium (He II) within Helium Tanks (HT), organized into pairs inside a Cryomodule (QM).  Each QM is connected to a dedicated Cryogenic Valve Box (QVB).  The combination of one QM and one QVB is called a Cryo-Cell (QCELL).  The full LINAC configuration will comprise sixty CAVs in thirty QMs.  Initial deployment includes twenty-four QMs: the remaining six to be added later.

Cryogenic System

The Cryoplant (QPLANT), a subsystem of the Cryogenic System (Figure 1), is designed to provide refrigeration to QMs via the Cryogenic Distribution System (QDIST).

Figure 1 Overall layout of the Cryogenic System

QDIST comprises the QLM, the string of QVBs, and the QVE.  The QLM houses the main headers distributing cold helium at multiple temperature levels.  Each QCELL regulates its helium mass flow by tapping from and returning to the distribution headers.  Excess flow is bypassed through the QVE.

The QPLANT is distributed over different areas as shown in Figure 2:

Compressor Room: Location of the Warm Compression Station (WCS)

Storage Area (outside): Location of the helium storage vessels and (if needed) liquid nitrogen storage vessels.

Cold Box Room: Location of the QRB with the associated warm panel.

Connecting rooms: The Warm lines from the WCS to the QRB cross multiple other rooms.

Figure 2 View of the buildings related to the QPLANT.

Cryogenic Users

The Cryogenic Users (QCELL), as illustrated in Figure 3, interface with the QPLANT through a common set of designated helium process lines: A, B, D, E, and W.  The W-line is a warm (300 K) helium return line from the QCELL.

The Thermal Shield (TS) cooling presents a static heat load, regardless of the operational scenarios (2 K or otherwise).  The TS system utilizes high-pressure helium with a supply temperature of ~40 K and return temperature of ~60 K, forming a closed, passive thermal circuit that ensures radiation shielding and temperature stabilization

Each QCELL includes a 600 W heater in its 2 K tank.  These heaters support warm-up operations by evaporating residual liquid helium (isothermal phase) and increasing the enthalpy of the cold mass (reheating structural material)

Figure 3 Simplified interface diagram of the QPLANT depicting a single representative ‘QCELL’ (inside grey dotted line) as a proxy for all heat load sources.  Temperatures shown are indicative of the 2 K operating scenario.

Overview of the He lines

The QPLANT includes a WCS connected to helium storage vessels, a Cold Box for refrigeration processes, and process equipment for drying, oil removal, gas management, and purification.  An indicative Process Flow Diagram of the QPLANT is shown in Figure 4 with Table 1 providing descriptive details of the main interfacing and transport lines.

Table 1 Main interfacing and helium transport lines

| Family | Constituents | Functional role | Participation in cryogenic cycle |
| --- | --- | --- | --- |
| Cryogenic distribution lines | QRB.A, QRB.B, QRB.D, QRB.E | Deliver 4.5 K SHE, return 2 K vapor, and supply/return 40/60 K thermal-shield flow | Yes – core refrigeration circuits. Coldbox room transfer from QLM to QRB |
| Warm line interfaces | QINFRA.U, QINFRA.W, QINFRA.S | Utility GHe (U), warm coupler return (W), safety/vent path (S) | Partial – only W carries a steady liquefaction load; U and S are utility / contingency |
| Internal plant headers | WCS.HP, WCS.LP, WCS.VLP | HP feed to QRB, LP return, VLP suction; traverse multiple rooms and floor levels | Internal only, nevertheless routed through civil interfaces and therefore listed for coordination |

QINFRA.W is the only warm return in normal operation and represents the liquefaction load for the QPLANT.  This represents ~ 4 % of the Helium supplied by the QPLANT to the QCELL via the A-Line in nominal operation.

QINFRA.U is an ad-hoc utility supply and does not participate in the closed helium cycle under normal conditions.

QINFRA.S is a safety line used during abnormal or emergency events to protect system integrity (e.g., cold-box overpressure).  It routes the discharged gas to the LP suction interface of the HP compression stage, from which it is reintegrated into the WCS.HP header, preserving helium inventory, and ensuring pressure relief.

Figure 4 QPLANT’s simplified Process Flow Diagram

# Introduction to QPLANT Control & Interlock System, CIS services and infrastructure.

The QPLANT Control & Interlock System (QPLANT:CIS) shall manage all internal process operations and local safety functions of the QPLANT.  It comprises the WCS-room PLC, the QRB-room PLC, and a Test and Development Station that physically and functionally mirrors the QPLANT:CIS hardware

The MINERVA Control and Interlock System (CIS) consists of the following two parts:

MINERVA Control System (MCS) for the control and monitoring of all accelerator components (including QCELL) and interfaces with QPLANT:CIS.

MINERVA Interlock System (MIS) executes machine and personal protection interlocks and is split into two parts:

  - DIS for machine protection: It is e.g., used to communicate any machine protection relevant interlock from/to the QPLANT to/from QPLANT external systems, e.g., loss of cooling water flow of the SCK CEN infrastructure, loss of insulation vacuum of the QMs.

  - PEPS for personal protection: It is e.g., used to communicate any personal protection relevant interlock from/to the QPLANT to/from QPLANT external systems e.g., oxygen deficiency

The MINERVA IT Infrastructure (MIT) provides the supporting IT infrastructure for the entire facility.  For the QPLANT, this includes providing essential functionalities to its Control and Interlock System (QPLANT:CIS), such as user authentication, standard network backbone, …

Figure 5 QPLANT - Control and Interlock related systems

Nature of the Procurement

Scope of Work by the Contractor

The Contract scope covers all services required to design, build, and commission a fully functional QPLANT in compliance with the requirements stated in this document.  The scope of work includes, but is not limited to, the following activities:

Design & engineering (including QPLANT internal process integration)

Manufacturing, procurement, and supply of all components

Transportation, delivery, and on-site installation

Stand-alone commissioning and testing, including QPLANT:CIS

Quality assurance and quality control activities

Support service (based on time and material)

- N.B.: Integrated commissioning activities that involve end-user participation (e.g. CIS interfacing or operational acceptance testing by SCK CEN personnel) are outside the Contractor’s scope.

Scope of Supply by the Contractor

Fixed Scope

- One (1) fully functional Cryoplant

  - including e.g.

    - Warm Compression Station (WCS)

    - Refrigeration Cold Box (QRB)

    - Internal piping and vacuum systems

    - Control and interlock system (QPLANT:CIS)

  - excluding

    - Helium gas storage vessels of the Warm Storage Helium (WSH)

- Helium inventory for commissioning and acceptance testing

- Full documentation package

Contingent parts

- Set of strategic spare parts for the first 5 years

- Helium gas storage vessels of the Warm Storage Helium (WSH)

- Yearly Service Level Agreement (SLA)

N.B.: There is no order/preference assumed for the contingent parts.

Technical Requirements

Introduction

The Contractor shall be fully responsible for ensuring that the Deliverables and Services provided fully meet the specified requirements for the Contract.  Therefore, the Applicant shall duly analyse the SCK CEN’s Tender Documents and evaluate whether sufficient information is presented to allow the Applicant to put forward a proposal that ensures the delivery of the procured items meets the specified requirements.  If certain information is found to be lacking, the Applicant shall request this information from SCK CEN without undue delay (according to §1.6 of the Main Tender Document).

In accordance with §1.7 of the Main Tender Document, the Contractor may no longer rely on information lacking after submission of its offer.  If the Contractor identifies a lack of information during the performance of the Contract, this shall not give rise to any basis for a Variation.

In the offer, the Applicant shall explicitly list all additional requirements (beyond those specified by SCK CEN) which have been defined by the Applicant, and which are assumed to be necessary for fulfilling the intended function, performance, or integration of the proposed solution.  All such assumptions and requirements shall be clearly identified, justified, and documented as part of the offer.  These additional requirements may be used as a basis for the system design and/or verification.

The technical requirements imposed by SCK CEN (including, but not limited to norms and other standards, processes, and their parameters) applicable to the development, performance, and quality (inspections, tests, etc.) of the procured items are specified in the present document and all other documents referred to herein.  In principle, these requirements are mandatory, unless adjusted in accordance with the principles set forth in the subsequent paragraphs.

In the offer, the Applicant shall clearly state any deviation if certain technical requirements are not met (e.g. if a requested norm, standard, or preferred process parameter is not implemented), The Applicant shall provide a clear description and justification for the proposed alternative.

In the offer, the Applicant may suggest modifications to the technical requirements imposed by this document, where such modifications improve cost, reliability, safety, ease of use, or any other functional aspect of the QPLANT.  Each modification shall be supported by an assessment of its advantages and drawbacks.

In the offer, the Applicant shall:

- Submit a single offer, inclusive of all proposed modifications, representing the most optimal solution.  Multiple alternative offers shall not be permitted.

- Include an overview of the main Contract activities.  For each activity, the Applicant shall detail how requirements will be met, the selected processes and techniques that shall be implemented.

- Provide at least the details as requested in the present document.  If no detail level is defined in this document, the Applicant is to choose, based on its experience, the appropriate (level of) detail(s) to be provided in relation to the criticality and/or complexity of the activity.

During negotiations, deviations and modifications shall be discussed between SCK CEN and the Applicant.  SCK CEN reserves the right to refuse any deviation or modification at its sole discretion and without justification.  Only deviations and modifications with prior written approval from SCK CEN may be implemented.

Nominal Operational Scenarios

Lifetime and annual maintenance schedule

The QPLANT shall be capable to operate uninterrupted in 2K mode for at least 90 consecutive days

The maintenance schedule shall adhere to the following constraints:

- ≥ 6 months: ≤ 10 days in 2K standby

- ≥ 1 year: ≤ 20 days in 4.5K standby

- ≥ 5 years: ≤ 60 days in warm stop

- ≥ 10 years: ≤ 120 days in warm stop

The QPLANT shall have a lifetime of at least 40 years

The QPLANT shall support ≥ 50 warm-up/cool-down cycles (300 K ↔ 2 K)

Steady state operational scenarios

The QPLANT shall support the steady state operational scenarios defined in Table 2.

Table 2 Operational Scenarios

| Operational scenarios | Description |
| --- | --- |
| Warm Stop | QPLANT and QCELLS at ambient temperature |
| Thermal Shield Standby | All QCELLs at thermal shield temperature |
| 4.5 K Standby | All QCELLs around 4 K |
| 2 K Standby | All QCELLs at 2 K (no RF-operation) |
| 2 K Operation | RF-operation allowed |

In the 2 K operation scenario, the cavity bath is 2 K (saturated superfluid helium with 31 mbar), the thermal shields supplied at 40 K, and the coupler cooled between 5 K and 300 K. Backpressure control and heat load stability are critical for RF operation and a priority design (for controls) priority both for QCELL and QPLANT.

In the 2 K standby scenario, the same temperature conditions as in 2 K operation apply, except no dynamic heat load due to RF operation occurs.

Transient operational scenarios

The QPLANT shall support the scenario transitions given in Figure 6.

The QPLANT shall execute the transition using the capacity defined by the steady state scenarios.  No additional capacity shall be added solely for acceleration of state transitions.

Cool-down

The QPLANT shall perform the cool-down of the QPLANT simultaneously with the cryogenic users (QCELL and QDIST (static heat loads only).

The QPLANT shall facilitate parallel cool down/warm up of all QCELLs.  During cooldown and warm-up, cryomodules impose constraints:

- Magnetic shields must reach T < 70 K (part of the 50 K thermal mass) before cavities (part of the 2K mass) reach T < 10 K.

- The QCELLs will autonomously limit cooldown speed to enforce this requirement on the user side

The QPLANT shall facilitate an alternative cooldown in which only the thermal-shield (TS) circuit which contains the 50 K stage cold masses are cooled until their average temperature reaches 50 K.  Subsequently the headers A–B and D–E  are simultaneous cooled down

Figure 6 Operational scenarios and transitions for the Cryogenic System.  Blue boxes indicate steady states while light blue boxes indicate transients

In their offer the Applicant shall:

- Indicate and demonstrate the shortest achievable cooldown time from 300 K to 2 K using Appendix 9.1 data, and the warm-up duration for each transition in assuming simultaneous cooling of headers A–B and D–E.

- Indicate and demonstrate the maximum refrigeration power the QPLANT can sustain at 250 K, 200 K, 150 K, 100 K, 50 K and 4.5 K.

Warm-Up

The QPLANT shall facilitate the warm-up of the cryogenic users from 2 K to 300 K in less than 5 days.

The QPLANT shall support the transition shown in Cool-down

The QPLANT shall perform the cool-down of the QPLANT simultaneously with the cryogenic users (QCELL and QDIST (static heat loads only).

The QPLANT shall facilitate parallel cool down/warm up of all QCELLs.  During cooldown and warm-up, cryomodules impose constraints:

- Magnetic shields must reach T < 70 K (part of the 50 K thermal mass) before cavities (part of the 2K mass) reach T < 10 K.

- The QCELLs will autonomously limit cooldown speed to enforce this requirement on the user side

The QPLANT shall facilitate an alternative cooldown in which only the thermal-shield (TS) circuit which contains the 50 K stage cold masses are cooled until their average temperature reaches 50 K.  Subsequently the headers A–B and D–E  are simultaneous cooled down

for the warming-up of the cryogenic users, whether passively or actively (with QCELL heaters if available):

- “Warm-up to 4.5 K” by stopping the VLP Compressors (WCS/PVPS) and the Cold (QRB/CC)

- “LHe emptying” of the liquid helium baths by evaporation, optionally using electrical heaters, and stopping level controls

- “Warm-up to TS”

- “Warm up to Tambient”

In their offer, the Applicant shall indicate and motivate the expected duration of each main phase of the warm-up process.

Other operational scenarios

Purging and Conditioning

The Contractor may implement a manual purging, manual conditioning, and manual initial preparation of the QPLANT.

- If a manual approach is selected, the Contractor shall provide a detailed step-by-step procedure, including instrumentation checks, purge-gas quality requirements, vent routing, and acceptance criteria for oxygen-free readiness.

The QPLANT shall adhere to the purge-parameter table (pressure, flow-rate, duration, allowable residual O₂, N2 and H2O) provided by SCK CEN during contract execution.

Liquid Filling

The QPLANT shall facilitate an average retention rate of 0.8 g/s LHe per individual QCELL (24 g/s total) during the filling process.

During LHe filling, the QPLANT shall provide 2 900 L of LHe to the users.

The Contractor shall assume that LHe filling and emptying occurs when cryogenic users are at 4.5 K and header A conditions are met before JT expansion (as per QRB.A interface conditions during normal operation)

In their offer, the Applicant shall:

- State the expected duration of the LHe filling phase and the maximum LHe filling rate the QPLANT can produce.

- State the expected duration of the LHe emptying phase and the maximum continuous emptying flow rate the QPLANT can accommodate while preserving the helium inventory.

The Contractor shall facilitate the following two evaporation possibilities:

  - Static heat loads only (Minimum evaporation rate).

  - QCELL heaters sped up.

The emptying phase shall be considered both as part of the full warm-up sequence (2 K → 300 K) and as a stand-alone transitional operation (for example: 2 K Standby → 4.5 K Standby → LHe Emptying → Filled LHe Emptying →4.5 K Standby → 2 K Standby) to permit short maintenance windows.  See  for the state-transition diagram.

The helium inventory shall remain in QCELL and only be transferred to QINFRA storage for extended long-term unavailability (LTU) or planned access.  Any planned transfer of inventory shall:

  - Require specified monitoring and controls while inventory remains in QCELL (pressure/temperature telemetry, alarms, periodic leak checks).

  - Require documented isolation and valve configurations and confirmatory checks before any inventory transfer venting.

Performance Requirements

The QPLANT shall be sized for the following two Design Points:

  - Nominal Design Point: operational scenario “2K operation” with 30 QCELLs.

  - Minimal Design Point: operational scenario “2K standby” with 24 QCELLs.

The QPLANT shall be designed for the heat loads defined in Table 3.

Table 3 Heat Loads Summary from QCELLs and Cryogenic Distribution

| Operational Scenario | Isothermal Heat Loads [W] |  | Non-Isothermal Heat Loads [W] |  |  |  | Indicative Equiv. Refrigeration Power, [W @ 4.5K] |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Bath at 2K (qCAV) | Bath at 4K (qCAV) | VLP return line 3.5K-3.7K (qIB) | SHe supply line 4.5K (qIA) | TS (40-60K) (qTS+ qIE + qID) | Mass Flow (g/s) for couplers 4.5-300K (qCPL) |  |
|  |  |  | QRB.B | QRB.A | QRB.D, QRB.E | QRB.W (via QINFRA.W) |  |
| 2K Operation for 30QM: Nominal Design Point | 900 | 0 | 40 | 20 | 8600 | 2 | 3430 |
| 2K Standby for 24QM: Minimal Design Point | 340 | 0 | 30 | 10 | 5100 | 1 | 1490 |
| 4.5K Standby for 30 QM | 0 | 560 | 0 | 11 | 8600 | 2 | 1640 |
| TS Standby for 30QM | ~0 | ~0 | ~0 | ~0 | 8600 | ~1 (40k-300k) | 720 |

The QPLANT shall support the fluid conditions at the QRB interface for HP-A, VLP-B and CPLR-W listed in Table 4.

For the Thermal Shield circuits (QRB.D and QRB.E) the Contractor shall optimize the mass flow, temperatures, and pressures to improve the overall efficiency or capital investment.  The respective values listed in in Table 4 are the only indicative values.

In the offer, the Applicant shall indicate the temperatures, and pressures of the Thermal Shield circuits.

Table 4 Fluid Conditions at the Refrigerator Cold Box Interfaces for Different Operating Scenarios

| Interface QRB | High Pressure (HP) – QRB.A | Very Low Pressure (VLP) – QRB.B | Coupler Return (CPLR) – QRB.W | TS Supply – QRB.D | TS Return – QRB.E |
| --- | --- | --- | --- | --- | --- |
| Operating Scenario: 2 K Operation |  |  |  |  |  |
| Pressure (bar) | ≥ 3.0 | ≤ 0.026 | ~ 1.1 | ~ 14.0 | ~ 13.0 |
| Temperature (K) | ≤ 4.5 | ≥ 3.5 | 300 | ≤ 40 | ≤ 60 |
| Mass Flow Rate (g/s) | ≥ 47 | ≥ 45 | ≥ 2 | 81 | 81 |
| Operating Scenario: 2 K Standby |  |  |  |  |  |
| Pressure (bar) | ≥ 3.0 | ≤ 0.029 | ~ 1.1 | ~ 14.0 | ~ 13.0 |
| Temperature (K) | ≤ 4.5 | ≥ 4.2 | 300 | ≤ 40 | ≤ 60 |
| Mass Flow Rate (g/s) | 18 | 17 | 1 | 48 | 48 |

Reliability Requirements

The QPLANT shall apply proven processes and be based on industrially proven technologies.

For failures resulting in an unplanned transition out of the “2K operation” scenario, the MTBF shall be higher than 5 years.

For failures resulting in an unplanned transition to the “4.5K standby” scenario, the MTBF shall be higher than 10 years.

For failures resulting in an unplanned warm up of the linac to > 4.5K, the MTBF shall be higher than 15 years.

In the offer, the Applicant shall provide a substantiated justification for the MTBF of the QPLANT, including but not limited to:

- Applied redundancy (e.g., N+1, 2oo3)

- MTBF values for each critical component, with supporting data

- Summary RAMI considerations and lifecycle-impacting design choice

- Outline of RCM strategy supporting availability objectives

- Key failure modes and corresponding mitigation measures (FO, FC, NO, NC for critical isolation or segmentation valves shall be provided for the LOOP and at least one other scenario (main interfacing valves of QRB and WCS)

The Contractor shall submit the detailed MTBF calculation demonstrating the compliance of the detailed design with the MTBF requirements to SCK CEN for review and subsequent approval at the latest by the end of the Phase 1.  The Contractor shall substantiate the MTBF values by manufacturer data (OEM or COTS), field performance records, or predictive reliability models.  The level of detail shall be proportionate to the component’s criticality in the overall system reliability and availability architecture.  The Contractor shall also provide a component-level (LRU) replacement schedule for the expected lifetime duration of at least 40 years, including MTBF data, estimated downtime impact, and cost per intervention.

Reliability Centred Maintenance & Lifecycle Cost Management

The Contractor shall deliver a Reliability-Centered Maintenance (RCM) Plan.  It shall contain a MTBF analysis, inspection/replacement intervals, and spares recommendations for each system component.  For each individual component, the RCM shall state the proposed maintenance strategy (run to failure, time-based or condition-based).

- Functional verification (testing)

- Preventive Functional Test Plan RCM plan

The Contractor shall implement a Lifecycle Cost Management (LCM) strategy in alignment with a fixed-price contractual framework.  The LCM shall support informed decision-making across the full system lifecycle.

The LCM strategy shall integrate the following cost domains as per ISO 15288:2023:

- Capital Expenditure (CAPEX)

- Operational Expenditure (OPEX)

- Maintenance forecasting and spares planning

- Upgrade and obsolescence strategy

- End-of-life and disposal provisions

The Contractor shall document compliance with ISO 15686-5 (Lifecycle Costing), IEC 60300-3-3 (Reliability-Centred Maintenance), and ISO 55000 (Asset Management) in the definition of the RCM and LCM strategy.

- In the offer, the Applicant shall include, a brief dossier supporting the proposed RCM and LCM approach.  This dossier shall include:

- Summary of the proposed RCM strategy (e.g. run-to-failure, time-based, condition-based)

- MTBF values for major QPLANT and QPLANT:CIS components

- Spare part strategy and indicative critical inventory items

- Expected OPEX contributors (e.g. electricity, labour, (liquid nitrogen)

- High-level process-flow & safety-integrity summary (PFD/SIL)

- If a modelling tool (e.g. process twin or diagnostic simulation) is offered, outline the expected benefits, any additional hardware/software (BoM) and incremental cost; if no model is offered, provide a brief rationale and alternative diagnostic approach

- Planned maintenance & diagnostic activities for a five-year horizon

- A clearly labelled item “RCM & LCM implementation” in the fixed-price breakdown.  If already included in the lump sum, the Offer shall state “included in lump sum – no separate charge.”

QPLANT Design & Build Requirements

In the offer, the Applicant shall describe and justify the system architecture and configuration and provide the key specifications of the main components.

Units

All pressure values shall be stated as absolute values in bar(a) or mbar(a)

All other units shall follow the International System of Units (SI), with exception of flow in g/s (not kg/s)

3D Model

The Contractor shall deliver a detailed 3D CAD model of the QPLANT and associated components to ensure interoperability, detailed design accuracy, and lifecycle integration:

The Contractor shall submit a preliminary 3D model in the Concept Design phase.

  - The file format shall be STEP AP242 format

  - The Level of Detail (LOD) shall be at least LOD 200.

  - The model shall include a first indication of the location of all external interfaces (to SCK CEN support systems and infrastructure and QLM)

The Contractor shall submit an updated 3D model in the Final Design phase.

  - The file format shall be STEP AP242 format.

  - The 3D model shall include metadata such as component IDs, geometric data, material properties, kinematic information, assembly information.

  - The Level of Detail (LOD) shall be 400 (final installation-ready models).

  - The models shall include the terminal points to the SCK CEN provided site infrastructure and support systems (water cooling, MIT, ….).

The Contractor shall submit an as built 3D model before the SAT.

  - The Level of Detail (LOD) shall be LOD 500 (operational/as built model)

In the offer, the Applicant shall:

- Present the tools that he shall implement to allow SCK CEN to review the models (SCK CEN internally uses BIMS 360 and PTC CREO).

- Provide a preliminary model of the QPLANT with at least LOD 100 in STEP AP242 format.

Energy-efficiency

The QPLANT shall have an invCOP ≤ 380 W/W  at the Nominal Design Point.

Any deviation greater than 5% from the claimed inverse COP at final acceptance shall trigger contractual review, including performance non-conformity, penalties, or corrective actions.

In the offer the Applicant shall state and substantiate the invCOP for all operational scenarios, both for initial (24 QCELLs) and nominal design (30 QCELLs) configurations.  Lower invCOP values are considered an advantage.

The Contractor shall validate compliance of the QPLANT to the invCOP that the Contractor committed to in their offer at each contractual stage and report it in every design reviews The Contractor shall apply mutually agreed calorimetric, flow-based, or standardized test methods (e.g., ISO 5167, EN 13445).

In the offer, the Applicant shall

- Include the electrical power measurement method they will apply within the QPLANT, specifying the level of integration (e.g., total plant consumption including auxiliaries, compressors, control systems) and the measurement uncertainty.

- Specify the corresponding reciprocal measurement methodology expected to be applied by SCK CEN, to validate claimed energy figures.

Helium Inventory Management

The QPLANT shall minimize the loss of helium in all operation conditions (including failure modes).

In normal operation, the QPLANT shall loose at maximum 1Nm3 of He per day.  The overall leak rate measurable instantaneously for entire system shall be smaller than 1×10⁻⁵ mbar·L/s.

- This value shall be validated during FAT

The Contractor shall implement a helium leak detection and monitoring system in accordance with EN 13185:2001, Clause 6.2 (Leak Detection Methodology) or equivalent, including routine leak testing and automated isolation mechanisms.

The leak rates (including all interconnecting piping, joints and components operating at Operating Pressure and ambient temperature) shall not exceed the values defined in Table 5.  The system shall be qualified for leak-tightness under operational and standby conditions.

Table 5 He Leakage requirements (excluding via permeation and diffusivity)

| Type of Leak | Maximal leak rates |
| --- | --- |
| Per helium circuits to vacuum | 1×10⁻⁸ mbar·L/s |
| Per helium or helium-oil circuits to the water circuits | 1×10⁻⁸ mbar·L/s |
| Per LN2 circuit to helium circuits | 1×10⁻⁸ mbar·L/s |
| Per helium guard to sub-atmospheric circuits | 1×10⁻⁵ mbar·L/s |
| Per from helium and oil circuits to atmosphere | 1×10⁻⁵ mbar·L/s |
| Combined leakage from all heat exchangers of the cold boxes to vacuum vessel | 1×10⁻⁵ mbar·L/s |
| Combined leakage from all helium circuits to vacuum vessels | 1×10⁻⁵ mbar·L/s |
| Leak rate through a valve seat | 1×10⁻⁴ mbar·L/s |
| Leak rate from a valve to atmosphere | 1×10⁻⁵ mbar·L/s |
| Leak rate from a valve to vacuum | 1×10⁻⁸ mbar·L/s |

In the offer, the Applicant shall explicitly quantify and elaborate:

- Expected global local leak rates, including diffusive losses expressed as % loss per year.  Estimated number and types of valves and fittings contributing to leak paths.

- Type of helium leak detection methods, pressure hold test procedures, vacuum decay, or rise time methodologies, and long-term monitoring techniques.  Acceptance criteria for each method and the calibration procedure for leak detection equipment.

- Post-installation and operational phase monitoring strategy, if applicable, including thresholds and frequency

- Expected losses of helium during conventional pump, purge, and conditioning (QPLANT only) and user estimation based on internal volume (total pipe length and 90 l per cavity)

The Contractor shall calculate the total helium inventory required for the Cryogenic System, including QPLANT and all helium users listed in Table 6.

Table 6 Helium Inventory

| Component | Helium inventory data | Helium Mass (kg) |
| --- | --- | --- |
| Cryomodules (QM) including QVE. | QM (~ 90 litres of helium per cryomodules) +QVE ~ 200 litres | 440 |
| Cryogenic distribution: QVB and QLM for 2K operation | VLP return ~ 2 kg SHe supply ~ 15 kg TS supply-return ~ 12 kg Warm He lines ~ 1 kg | 30 |
| QPLANT | To be determined by the Contractor of the QPLANT | TBD by Contractor |
| Gaseous warm storage | Remaining inventory during operation. To be determined by the Contractor of the QPLANT | TBD by Contractor |

Abnormal conditions

In case of an abnormal event, no more than 1% of inventory shall be lost.  To this end, the Contractor shall implement a comprehensive helium recovery strategy covering all credible initiation events, including but not limited to LOOP, Loss of Vacuum or Instrument Air, Cooling Circuit Trip, Turbine Trip, QRB Trip, HP Compressor Trip, and PVPS Trip.  For each scenario, the Contractor shall identify at least:

- The required recovery mechanisms (e.g., buffer storage, valve isolation, overpressure protection),

- The stepwise action plan to resume normal helium circulation once the initiated event is resolved.

- The strategy shall be supported by engineering justifications and include timelines, buffer sizing assumptions, and any control system responses.

In case of a LOOP event, the following shall apply concerning the Instrument Air Supply:

  - SCK CEN will continue to supply the Instrument Air for initial valve actuation (Fail-Closed or Fail-Open).  However, this does not constitute a continuous supply obligation during LOOP.

  - The QPLANT shall contain a pneumatic backup system to allow helium recovery operations during a LOOP event.  It shall have a minimum autonomy of 6 hours under full helium recovery load conditions

- The pneumatic backup system be commissioned and functionally tested during the SAT under simulated LOOP conditions to verify switching, autonomy, and integration with the helium recovery sequence.

Helium recovery

The Contractor shall implement a comprehensive helium recovery strategy able to cope with the following He flow from the users:

- 200 g/s (300 K, ~1.2 bar) for the enveloping LOOP event mass flow

In the offer the Applicant shall present a high-level description of the helium recovery strategy including but not limited to a Bill of Materials (BoM) of all recovery components, including low-pressure gas balloon storage and/or high-pressure compressor-driven recovery options and/or dedicated purification system.

In the offer, the applicant shall indicate what Structures Systems and Components (SSC), or other design provisions required to contain/minimize all helium losses to no more than 1% of total inventory.

The QPLANT shall have an input to the QRB-S where the QCELL safety valves shall discharge to via the QINFRA-S line.

Warm Storage Helium

Overview of System

The Warm Storage Helium (WSH) is a system that provides storage, buffering, and management of warm helium gas within the QPLANT cryogenic process.  It acts as an intermediate reservoir between the Warm Compressor Station (WCS), the helium recovery system, and purification units ensuring stable operation during start-up, shutdown, transient modes, and maintenance.  The WSH allows for pressure balancing, helium inventory control, and gas recovery under all operating conditions, thereby maintaining system integrity and operational efficiency (see Figure 7).

Figure 7 WSH with Contingent Part 2 (area covered in purple dotted line)

The Warm Storage Helium (WSH) consists of:

Helium storage vessels (Contingent Part 2)

Associated infrastructure (support structures, cat ladders, ….), Contingent Part 2.

Interconnecting piping between these vessels and the WCS (WCS.LP, WCS.HP)

Interconnecting piping to dedicated recovery system and/or purification system (if applicable)

Associated instrumentation, valves, and control equipment.

Make-up line to external gaseous helium delivery

Scope and Contingency Definition

This Contingent Part 2 covers the supply and installation of the helium storage vessels and their associated infrastructure on the SCK CEN site.  The Fixed scope of the Contract covers all the remaining parts/activities.

General WSH  requirements

The WSH shall be dimensioned to store the full helium inventory plus 20 % margin.

The WSH shall be divided into a minimum of three (3) helium storage vessels to ensure operational flexibility, maintainability, and robustness during cyclic operation or partial unavailability of vessels.

The set pressure (PS) of the WSH relief devices shall be ≥ the maximum operating pressure of the HP header and ≤ the MAWP of the WSH vessels.

The helium storage vessels shall be installed outdoors and oriented vertically to minimise footprint in accordance with [AD 2].  The final layout, volumes, and positioning shall be proposed by the Contractor and validated by SCK CEN during the conceptual design phase.

Each helium storage vessel shall include at least one inspection manhole to permit internal access for periodic inspection.

The Contractor shall prepare a technical specification for the helium storage vessels as per [AD 14] covering surface cleaning, corrosion protection, inner-surface treatment (e.g., Rustol/Owatrol or equivalent), outer-surface coating,

Each vessel shall be fitted with valves and ports required for purging, conditioning, and gas analysis.

The storage vessels shall be interconnected by valves and connected to both the LP and HP sides of the WCS via automatic valves to regulate process pressures.

A gas-management warm panel for controlling the helium storage vessel valves shall be integrated into the main control panel of the WCS.  This panel shall allow local operation of valve switching, isolation, and vessel selection functions associated with the helium storage system.

At least the measuring points defined in Table 7  shall implemented and be remotely read out by the QPLANT:CIS.  Each vessel shall also be equipped with a local pressure indicator

Table 7 Measuring points for gas helium storages.

| Parameter | Measurement Location(s) |
| --- | --- |
| Temperatures | Temperature of at least one storage vessel |
| Pressure | Helium pressure in each installed helium storage vessel Helium pressure in the common manifolds |
| Impurity measurements | Pick-ups and capillaries shall be provided for measuring moisture and nitrogen contents in each vessel |
| Local indicative measuring points | Helium pressure indicator for each installed vessel |

Scope boundary between Fixed and Contingent part

Even if this contingent part is not exercised, the Contractor shall execute:

Preparation of functional and technical specifications for the storage vessels (e.g.: volume, flanges, instrumentation ports, dimensions, surface treatment, …).

Physical and functional integration of the helium storage vessels within WSH

Definition of instrumentation and remote read-out points

Supply and Installation of all instrumentation on the vessel

Piping, valves, and valve logic between the helium storage vessels (and any other WSH interface points) and the WCS

Overall system and control integration within the WCS control logic

Provision of all physical connections to the vessel interfaces, irrespective of the contingent assignment.

If Contingent Part 2 is exercised, the Contractor shall also:

be fully responsible for the design and mechanical verification of the helium storage vessels.

submit the mechanical support design data and vessel interface loads as part of the detailed design deliverables.

Warm Compressor Station

WCS General Requirements

The Warm Compressor Station (WCS) shall facilitate helium compression across at least three pressure levels:

- VLP (Very Low Pressure)

- LP (Low Pressure)

- HP (High Pressure)

The WCS shall be connected to the warm gas helium storage (WHS).

WCS Valve Requirements

A minimum of one bypass valve shall be installed between each pair of pressure headers (VLP ↔ LP and LP ↔ HP).  Each bypass valve shall be sized to pass ≥ 100 % of the maximum steady-state mass-flow rate of the associated compressor train under the worst-case differential-pressure condition.

A control valve shall be installed in the connection from the helium-gas storage to the LP suction header for loading.

A control valve shall be installed in the connection from the HP discharge header to the helium-gas storage for unloading.  This valve shall be installed downstream of the fine dust filter after the oil charcoal adsorber.

All helium connections between the WCS and the QRB shall be routed through control valves located inside the WCS building to limit pressure-transient rates to values approved by SCK CEN.

Suction and discharge lines of every compressor stage shall be fitted with non-return valves that automatically close when the compressor stops.

Noise level

The sound-pressure level of each compressor shall not exceed 80 dB at 1 m during any steady-state operating mode.  Noise tests shall be performed for each compressor and its electric-motor drive in accordance with ISO 2151 (or an equivalent international standard) after FAT and after SAT, and reports shall be submitted to SCK CEN.  The results shall be documented in reports which shall be submitted to via VLAREM dossier

- In the offer, the Applicant shall state guaranteed per-unit and complete-skid noise levels at 1 m, describe the envisaged noise-mitigation elements (e.g., acoustic enclosures, intake/exhaust silencers, isolation mounts), and identify the configuration to be used for FAT/SAT noise tests.

Vibration level

The maximum vibration levels of the compressors and other rotating machines shall comply to ISO 2372 (or its successor ISO 20816).  During the design phase, the Contractor shall submit a vibration-analysis report and calculation dossier for SCK CEN approval.  During SAT, the Contractor shall measure the vibration using calibrated instruments and test methods in accordance with ISO 2954.

Compressors requirements

There shall be at least three (3) compressors per compressor stage with the number based on flexible operational for the design case mentioned in Table 3 that cover the design  flow.

All compressors of one compression stage shall identical.

The HP compressor coupling shall comply with API 671 / ISO 10441 (or equivalent).  See Figure 8 for details

Figure 8 Direct Drive

Each compressor skid shall include an oil-retention reservoir sized to contain the full oil inventory of the skid in the event of pipe rupture.

Each compressor shall have an internal slide-valve control providing stable turndown to ≤ 30% of rated mass flow (nameplate flow at rated conditions) without surge or recycle over the specified operating pressure range.

Each compressor motor shall be equipped with a variable-frequency drive (VFD) rated for full-load current.

The VFD speed control shall provide primary capacity turndown; the internal slide valve shall provide trim control and anti-surge stabilization across the operating range.  The control strategy shall minimize power consumption in all load conditions.

In the offer, the Applicant shall state the number of LP compressors and HP compressors and confirm the long term sustainable operating frequency.

Coolers

On the gas side, each cooler shall include purge valves suitable for nitrogen blow-through or helium rinse.

On the water side, valves to drain the water and to purge the air shall be installed.

A manual or thermostatic control valve shall be installed at the outlet of each cooler to regulate the water flow.

A manual water shut off valve shall be installed at the inlet of each cooler.

Oil

The Contractor shall supply all required compressor oil for the first filling.  The particle size shall not exceeding 25 µm and the water content less than: 100 ppm v/v for Okt Alkyl Olefins (PAO), 1000 ppm if standard Breox type

In the operation and maintenance manual, the Contractor shall include:

  - detailed procedures for oil preparation, dehydration, and filtration.

  - the sampling frequency for the routine oil-analysis

  - specifications and acceptance limits for particle count, water content and acid number.

Oil circulating system

Oil-pump units

Each compressor shall be fitted with a dedicated, automatically controlled auxiliary oil pump unit that maintains the minimum bearing-lubrication pressure during start-up, shutdown, and coast-down.

Each auxiliary oil-pump unit shall be equipped with suction and discharge pressure transmitters and a flow switch which interlocks the compressor protection system.

Oil-retention vessel

Each oil-retention vessel shall be fitted with an electric heater to pre-heat the oil prior to compressor start-up.

Each oil-retention vessel shall include a differential-pressure indicator across the internal separator to allow fouling monitoring.

The Contractor shall provide suitable sampling points and agreed measurement procedures at the outlet of each phase separator to allow verification of the oil content during performance tests and during long-term operation.

The helium gas at the outlet of each phase separator shall have an oil content not exceeding 100 ppm (weight) under all normal operating conditions.

- The oil retention vessel and associated oil removal system upstream of the phase separator shall be designed and sized such that the requirement in  is met over long-term continuous operation, without degradation of performance that would lead to exceeding 100 ppm (weight) of oil at the phase separator outlet.

The Contractor shall provide suitable sampling points and agreed measurement procedures at the outlet of each phase separator to allow verification of the oil content during performance tests and during long-term operation.

The design, sizing, and performance guarantees of downstream coalescers and absorbers shall be based on a maximum inlet oil content of 100 ppm (weight) at the oil retention vessel / phase separator outlet.

Oil filters

The inlet of each compressor oil-pump shall be protected by duplex (change-over) filters rated 25 µm absolute, mounted in parallel.

A fine oil filter shall be installed at the injection points of compressor bearings and shaft seals.

Manual shut-off valves shall be installed upstream and downstream of every oil filter.

A differential-pressure gauge shall be provided across each oil filter to give a visual indication of filter blockage.

Oil Purge and fill up requirements

Each compressor shall be equipped with manual isolation valves in all connecting piping to permit full circuit isolation for maintenance.

The Contractor shall design the purge system and slope all relevant piping at a minimum gradient of 1 % toward designated oil traps to prevent migration of oil into oil-free regions.

Oil Removal System (ORS)

Coalescers

Downstream of the HP primary oil removal system, at least three coalescing filters shall be installed in series, with dimensions such that sufficiently low gas velocity is achieved through the filter elements for efficient coalescing.

The Coalescer shall be designed with a 20% gas velocity margin.

The coalescer arrangement and its seal construction shall be capable of withstanding compressor vibration.

All coalescers shall be equipped with a standpipe on which magnetic level indicator is positioned.  The level shall be monitored locally and remotely.

The oil collected from the first two coalescers is to be re-injected to the suction side of the LP/HP compressors.  The automatic flush of oil from the coalescer to the compressor suction shall be carried out using a motorized valve controlled by the level indicator mentioned above.

The last coalescer operates as guard unit.  Any sign of oil collected therein shall lead to a shutdown of the compressor station.

The coalescers shall reduce the oil content of the stream to less than 40 ppb.

Charcoal adsorber

The charcoal adsorber shall be designed with a 20% gas velocity margin.

Only cleaned and dried charcoal in the form of smooth pellets shall be used as adsorbent filling.  No filling consisting of irregularly broken particles shall be used.  The filling of the bed shall be regular and no preferred paths for the helium may exist.

The Charcoal adsorber shall reduce the oil content of the stream to less than 10 ppb.

The Contractor shall demonstrate (based on design and previous experiences) that any movement of the adsorbent and the carry-over of dust particles is avoided.  E.g. the flow direction of the gas through the charcoal bed shall be from top to bottom.

The Contractor shall supply any equipment necessary to fill the adsorber without degrading the adsorbent.

The Contractor shall supply the heating unit necessary for drying the charcoal.

Helium dryer

The dryer shall remove water in the helium to less than 1 ppm.

The dryer shall generate a total pressure drop of less than 0.5 bar.

The adsorbent material shall be a molecular sieve of alkali alumina-silicate (Zeolite) or equivalent.

The helium drying system shall comprise at least two identical helium dryers installed in parallel.

The arrangement shall allow continuous drying of the full HP total helium mass flow with one dryer in operation while the other is in regeneration or unavailable.

Each helium dryer shall be dimensioned for the full helium mass flow (HP total mass flow) contaminated with up to 50 ppm by volume of water for a duration of at least 12 hours before regeneration is required.

The regeneration shall be performed by circulation of warm and dry nitrogen gas.

The regeneration time for any helium dryer, including cooling and return to service, shall not exceed 12 hours.

The helium dryer shall be dimensioned for the full helium mass flow (HP total mass flow) contaminated with up to 50 ppm by volume of water for a duration of 12 hours before regeneration.

The helium dryer unit shall include inlet and outlet valves and a by-pass circuit.

Gas Filters

The Contractor shall install at least the following gas filters:

- At the suction side of each compressor a wire mesh filter of 100 µm of retention ability.

- Downstream of the charcoal adsorber, an adapted wire mesh filter to stop particles of charcoal adsorbent shall be installed.

- At the dryer outlet, a wire mesh filter of 30 µm shall be installed to trap particles of dryer adsorbent.

Each gas filter shall be equipped with manual shut-off valves on both sides of it to minimize contact with air.

Measuring points

At least the measuring points defined in Table 8 shall implemented and be remotely read out by the QPLANT:CIS.

Table 8 Measuring Points for WCS

| Parameter | Measurement Location(s) |
| --- | --- |
| Helium Mass Flow Rate | -WCS.VLP -WCS.LP -WCS.HP |
| Helium Temperatures | -WCS.VLP -WCS.LP -WCS.HP |
| Helium Mass flow rate | -WCS.VLP -WCS.LP -WCS.HP |
| Helium Pressure | - Suction of each compressor (including VLP) - After each oil-retention vessel - After the charcoal adsorber and the dryer - Each warm storage vessel |
| Differential Pressure | - Across each oil filter - Across the charcoal adsorber and the dryer |
| Moisture | - After the charcoal adsorber - Upstream and downstream of the dryer - At 2/3 height of the dryer bed |
| Nitrogen Content (for Air Detection) | - Inlet of LP stage of HP compressor - After the dryer |
| Oil Level (Analogue and Switches) | - In each oil retention vessel (analogue and switch) - In the third coalescer (switch) |
| Water flow rate | - At the outlet of the coolers |
| Water pressure | - At the inlet of the coolers |
| Motor temperature | - Each motor |
| Vibration | - Each Compressor |
| Operation-hour counters | - Each Compressor, oil pumps, other pumps |
| Oil level | - Oil retention vessels and third coalescer |
| Oil injection pressure | - Each compressor skid |
| Rotational speed | - Compressors |
| Current and voltage | - Each motor and compressor |

Refrigeration Cold Box

The Refrigeration Cold Box (QRB) comprises internal and external components and produces the refrigeration power necessary to achieve the needs of the cryogenic users.  The QRB is coupled to the WCS and distributes the cryogenic flows to the Cryogenic Distribution System (QDIST).

General Requirements

In the offer, the applicant shall provide a preliminary 3D MODEL including the terminal points for the QRB-A/B/E/D lines.

The QRB shall be a horizontal cold box to fit with the building constraints (see [AD 2]).

The QRB shall comprise the following internal components:

- Heat exchangers

- Turbines

- Cold Compressors

- Piping

- 80 K dual bed adsorber

- 20 K single bed adsorber

- Helium baths at 4.5 K and 2 K

- Filters

- Heaters

- Cryogenic valves

- Instrumentation

The QRB shall comprise the following external components:

- Vacuum pumping system.

- Warm panel with warm valves and instrumentation.

- Piping and valves for purging and conditioning all the circuits.

- Electrical cabinets.

- Safety valves.

- Helium guard circuits.

- Compressed air distribution.

- Coolers for turbines.

- A platform for easy access to all the components located at the upper level.

- Connection port to transfer liquid helium from QRB to external dewar or vice versa.

The Contractor may employ liquid-nitrogen pre-cooling between 300 K and 80 K.  If liquid-nitrogen pre-cooling is adopted, the Contractor shall supply, integrate, and warrant all associated equipment, controls, and interfaces.

In the offer, the Applicant shall submit a quantified techno-economic justification demonstrating overall benefit of the liquid-nitrogen pre-cooling.  The justification shall, as a minimum, include:

- Capital-cost comparison (EUR).

- Operating-cost comparison (EUR per year), including liquid-nitrogen consumption expressed in kWhₑ

- Impact on delivery logistics and supply reliability.

At least one manual shut-off valve shall be installed on each process line connected to the WCS, upstream of the first cryogenic isolation device.

Main components

Vacuum vessel(s)

The vacuum vessel(s) shall be designed for full internal vacuum (0 bara) and for an external overpressure of minimum 1.5 bar(g) unless otherwise justified by the safety study.

The design of the passage of every line (cold or warm) connected to the QRB shall avoid any condensation or frost formation at the interfaces during any operation scenario or any transition between operation scenarios.

The ports carrying cold valves, turbines, transfer lines connections and instrumentation feedthrough shall be fabricated from stainless steel.  The vacuum vessel(s) may be fabricated from mild steel.

The design of the pumping ports shall prevent the intake of any loose sheets of superinsulation into the vacuum pumps.

The QRB shall be equipped with a vacuum barrier at the Cryogenic Distribution System interface.

Helium Heat exchangers

Aluminium plate fin heat exchangers shall be vacuum brazed.  Stainless steel heat exchangers shall be of all-welded construction.

For all heat exchangers, the type and origin of materials and transition pieces (Aluminium-Stainless Steel) shall be provided.

All heat exchangers operating below 20 K shall be arranged vertically with the warm end at the top.

Any heat exchanger between 300 K and 80 K shall facilitate warm up and regeneration for frozen water removal in the HP side.

The differential pressure between inlet and outlet of any heat exchanger shall be measured to monitor the pressure drop evolution during operation.

In case of 80 K nitrogen pre-cooling, a separated heat exchanger between nitrogen and HP helium flow shall be installed to avoid solidification of nitrogen in case of return of cold helium flow in the LP stream.

Turbines

Turbines with gas lubricated or magnetic bearings shall be deployed.

The power extracted by the turbines shall be transferred to water cooled heat exchangers.  Acceptable materials for the water channels are stainless steel and copper compatible with the water quality as described in 3.8.2.2.  The water side shall give easy access for cleaning.

To allow the easy exchange of turbine cartridges, the system shall include all the elements needed to isolate, warm up, purge and cool down each turbine individually.  This exchange shall be possible in situ without warming up heat exchanger blocks.

A replacement of one turbine cartridge shall not exceed 3 hours.

- Separate vacuum barrier

Cold Compressors

Cold compressors may either be in the QRB or located in a dedicated Cold Box with separate vacuum

The compressors shall be centrifugal with active magnetic bearings.

The Contactor shall provide the pressure fields showing the pressure ratio as a function of the reduced flow for different reduced iso-speeds.  The stall and choke lines shall be indicated.

The mass flow rate of helium shall be easily adjustable via rotation speed regulation using Variable Frequency Drive.

The rotational speed of the cold compressor shall include at least 10% speed margin with respect to the maximum value encountered in the different operation scenarios.

The rotational speed of each cold compressor should allow to be lowered down to 30 % of the nominal speed while remaining in the operational window.

The Contractor shall submit detailed cool-down and start-up procedures for each cold compressor as part of deliverable DD-5.  The procedures shall be approved by SCK CEN before FAT

The cold compressors shall allow inspection, maintenance, and exchange.  The intervention time including the warm-up and cold compressor exchange shall be less than 4 hours.

Helium phase separators

Two helium phase separators shall be installed in the QRB: one at 2 K pumped by the cold compressors and one at 4.5 K.

The helium phase separators shall be sized for all operating scenarios.

The helium phase separators shall be equipped with electrical heaters to adjust the level of liquid helium, to empty from liquid helium and to simulate the user heat load during stand-alone commissioning and acceptance testing of the QPLANT.

A diffuser shall be installed at the inlet of the helium phase separators.

Adsorbers

To remove air impurities, two 80 K adsorbers shall be installed with an operating temperature below 85 K.

The two 80 K adsorbers shall be parallel switchable.

Each of the 80K adsorbers shall be sized to purify the full HP compressors flow contaminated up to 50 ppm by volume of air.

The Contractor shall choose the adsorption/regeneration time of the 80K adsorbers to guarantee continuous operation.

The system shall perform the switching, regeneration, and cool-down of the 80 K adsorbers fully automatically.  A by-pass between the outlet of the switchable 80K adsorbers and the LP line of the QRB shall be installed which could be used for helium purification.

To remove the remaining impurities of neon and hydrogen, one 20 K adsorber operating shall be installed with an operating temperature below 25 K.

This 20 K adsorber shall be sized to retain impurities of the full helium flow contaminated up to 1 ppm by volume of hydrogen and neon each, for a duration of at least 200 hours.

The system shall perform the regeneration of the 20 K adsorber fully automatically.

The regeneration and re-cooling of the contaminated 29K adsorber shall take less than 12 hours.

All adsorbers (80K and 20K) shall be equipped with a full mass flow by-pass.

The design of the adsorbers shall allow easy access for the periodic change of the adsorbent.

The design of the adsorbers shall avoid any movement of the adsorbent and any emission of dust.  The adsorbent material shall be chemically and mechanically stable under any operating conditions.

All adsorbers shall be equipped with gas analysis ports (§  3.6.7.3).

Filters

Downstream of each adsorber, a 10 µm wire mesh filter shall be installed.

Filters of 10 µm retention ability shall be installed at the inlet of turbines.

The Contractor shall decide the number and positions of any additional filters required.

All filters shall be accessible from the outside of the vacuum vessel for changing, cleaning, and purging.

All filters shall be designed to prevent dust collected can falling into the connected piping during replacement.

Heaters

The Contractor shall install heaters wherever necessary to permit a full warm-up of all the circuits, including cryogenic distribution and the cryomodules as described in 3.2.3.2.  Heaters shall also be used to demonstrate the QPLANT performance during the Acceptance Tests.

The Contractor shall specify the installed heating capacity (kW) and physical location of every heater.

Heaters and associated electrical wiring shall be designed to minimize the heat loads to cold surfaces using necessary thermalization and optimized wiring diameters.

Measuring Points

At least the measuring points defined in Table 9 shall implemented and be remotely read out by the QPLANT:CIS.  They shall be logged at a rate ≤ 1 Hz.

Table 9 Measuring Points for QRB

| Parameter | Measurement Location(s) |
| --- | --- |
| Helium mass flow rate | - Inlet HP stream of the QRB- Supply SHe from QRB to LINAC - Coupler mass flow return |
| Temperatures | - Inlets and outlets of the QRB - Inlet and outlet of each turbine - HP outlet downstream 300 K–80 K precooling - In each adsorber bed- Liquid helium baths |
| Pressure | - Inlets and outlets of the QRB - Inlet and outlet of each turbine - Outlet of each cold compressor - In each adsorber bed - Helium guard circuits (if any) - Liquid helium baths- Water cooling circuit |
| Differential pressure | - Across each filter or set of parallel filters - HP line (300 K–80 K) first heat exchanger - Across each adsorber bed (or as pressure at inlet and outlet) |
| Level measurements | - In liquid helium phase separate (2K and 4K) - In the liquid nitrogen bath (if applicable) |
| Moisture | - At the inlet of the QRB (HP flow) |
| Nitrogen content for air detection | - At 2/3 of the 80 K adsorber beds |
| Rotational Speed | - Rotational speed of each turbine |
| Vacuum Pressure | - QRB vacuum vessel |
| Electrical Power | - Electrical power of installed heaters - Electrical Power to Cold Compressors |

Purging

The Contractor shall install all the necessary equipment and connections required for the purging (venting, pumping, and filling) and conditioning of the QPLANT.

The helium pumped or vented shall be sent to atmosphere outside the buildings.

Design, Materials

Material Requirements

All materials shall be delivered with traceable certificates.

Cleaning and surface treatment

All welding and brazing surfaces shall be cleaned before assembly, using proper solvents and water to remove any trace of acid flux, organic depositions and any other dirt and dust.

All metallic surfaces in contact with He shall be cleaned, pickled, and passivated.  Prior to helium leak testing all involved components in contact with He shall once again be cleaning (degreasing, cleaning, and drying).

Bellows

Bellows to compensate thermal contraction shall be avoided through proper piping design.  If unavoidable, the Contractor shall seek SCK CEN approval for the location and type of bellows.

- In the offer, the Applicant shall include a preliminary list of unavoidable bellows (if any).

Joints and seals

Dismountable joints in the QRB below room temperature are not recommended and shall be subject to approval by SCK CEN.  At ambient temperature, metal and Viton O-rings are allowed.

Valve requirements

The cryogenic valves inside the QRB shall be of the extended-spindle type, sealing by metallic bellows.

All helium shut-off valves (independent of helium temperature) shall comply with the following requirements:

  - Valve Type Selection

- Ball valves shall be employed for nominal sizes up to and including DN100, unless otherwise justified by process or safety requirements.

- Butterfly valves shall be employed for nominal sizes above DN100, except where specific process conditions (such as full tightness at cryogenic temperature or throttling requirements) necessitate alternative selection.

  - Qualification and Documentation

- The Contractor shall submit documentation of type testing or qualification records demonstrating suitability for helium and cryogenic operation in accordance with EN 1626 and EN 12516-1/2 as part of the Conceptual Design file in LCP1.

  - Installation Requirements

- Shut-off valves shall be welded to the pipework and preferably to the top plates of the QRB.

Every control valves shall be equipped with:

  - electro-pneumatic positioners

  - a digital position-feedback.  This signals shall be continuously monitored by the QPLANT:CIS.

Manual on/off valves that are safety-relevant or operationally critical (as identified in the approved reliability and safety analyses) shall be equipped with two independent end-switches confirming their mechanical position (open/closed) during operation.  The Contractor shall submit the list of such valves for SCK CEN approval during the detailed-design phase.

Helium guard

Every component operating below atmospheric pressure shall be protected from air ingress by a helium guard filled with helium with a pressure higher than 1.05 Bar(a).

Each helium guard segment shall equipped with a manual isolation valve to help locate leaks.

The helium guard pressure shall be remotely monitored by a pressure transmitter which is connected to the QPLANT:CIS.

Each helium guard segment shall be equipped with an automatic on/off valve, controlled by the control system, to automatically re-establish the nominal helium guard pressure in case of a leak, to avoid air contamination and improve system availability.

All static seals, which are not welded and operating between atmospheric air and sub-atmospheric helium, shall be doubled.  The space between the seals shall have a connection to the helium guard system.

Insulation vacuum system of the QRB

The QRB shall be equipped with a dedicated vacuum pumping system.

The pump down of the QRB from atmospheric pressure to less than 10-5 mbar shall take less than one week.

The QRB vacuum shall be protected by a fast-acting isolation valve between the turbo pump and associated roughing pump.

A dedicated flange shall be provided between the Turbo- and associated roughing pump for connection of a leak detector.

The pump down of the vacuum system shall be fully automated.

All valve actuators and vacuum gauges shall fully exposed to MCS.

Pending completion of a risk assessment for asphyxiation hazards, if operation of the roughing pump presents an asphyxiation risk, the exhaust shall be routed outside the building via a dedicated pipe.  This requirement shall be confirmed and finalized no later than the Conceptual Design phase.

Instrumentation

The Contractor shall furnish and install all instrumentation required to:

- enable automatic control of all QPLANT operational scenarios.

- maintain safe operating conditions; and

- verify compliance with the specified performance criteria during acceptance testing.

- The Contractor shall demonstrate, by reference to internationally recognised calibration certificates or equivalent traceable documentation, that every measuring instrument supplied is suitable for its intended purpose.

The Contractor shall define the instrumentation layout and measurement ranges and submit the documentation to SCK CEN for review and approval at the Detailed-Design stage.

The complete, as-built wiring diagram of the instrumentation and control circuits shall be included in the Deliverables package.

The Contractor shall submit a complete set of documentation for each instrumentation element including but not limited to calibration curves, power rating, location, and protection set points (where applicable).

Heaters

Each electrical heater shall incorporate a temperature control ensuring the specified maximum sheath or process temperature is not exceeded.

Heating elements needed for normal control or operation shall either (a) be replaceable without breaking the insulation vacuum, or (b) be implemented redundantly.

Real-time heater power measurements shall be transmitted to the QPLANT:CIS for trending and alarm purposes.

All heater circuits shall successfully pass a dielectric test in accordance with applicable IEC/EN standards:

  - Test Stages

  - A dielectric test shall be performed after each major installation phase.

  - A final dielectric test shall be performed at hand-over.

  - Acceptance Criteria

  - No breakdown of insulation or abnormal leakage current shall occur under the specified test voltage and duration.

Temperature measurements

Temperature measurements (including the whole thermometry chain) shall meet the requirements listed in Table 10.

Table 10 Temperature measurement precision

| Nominal Temperature | < 30 K | 30 K to 120 K | > 120 K |
| --- | --- | --- | --- |
| Accuracy required for standard measurements | ≤ +/- 100 mK | ≤ +/- 500 mK | ≤ +/- 1 K |
| Accuracy required for high precision measurements | ≤ +/- 50 mK | ≤ +/- 300 mK | not applicable |
| Long term drift for the whole scale | ≤ +/- 10 mK per year | ≤ +/- 50 mK per year | ≤ +/- 100 mK per year |

For each temperature measurement, the Contractor shall submit a proposal of classification (standard or high precision as defined in Table 10) for review and approval by SCK CEN.

The cabling between each temperature sensing element and its associated signal conditioning device shall be designed and installed to ensure accurate, stable, and noise-immune signal transmission under all specified operating and environmental conditions.

- The Contractor shall employ shielded, twisted-pair conductors or functionally equivalent solutions to minimise electromagnetic interference (EMI), preserve signal resolution, and enable compensation of lead resistance when required by the selected measurement method (e.g. 3-wire or 4-wire RTDs).

- The Contractor’s selected cabling solution shall be justified by reference to recognised standards or design practices, such as IEC 60751, IEC 60359, ISA RP12.6, or other EMI mitigation guidelines accepted in industrial instrumentation.  Temperature elements outside cold boxes shall be mounted directly in the fluid stream, using a protection tube welded on the pipe.

Pressure measurements (incl. vacuum gauges)

Each pressure transmitter shall be installed with at least:

- one isolation valve to allow safe removal, calibration, or replacement without depressurizing the connected volume or interrupting vacuum operation

- one dedicated connection for calibration or venting, also fitted with an isolation valve.

Each differential pressure transmitter shall additionally be equipped with a bypass valve and calibration valve.

The Contractor shall define the measurement ranges of all pressure instruments and submitted as part of DD-4.  Special attention shall be given to the Very Low Pressure (VLP) lines.

All pressure transmitters shall withstand, without de-calibration or damage, any pressure from vacuum up to the Operating Pressure defined by the relevant safety valve setting.

Accuracy of measurement shall comply with:

- Long-term drift of pressure instruments shall not exceed ±0.5 % of the maximum span per year.

- The accuracy for absolute pressure measurement shall be better than ±0.5 % of the calibrated span.

- The accuracy for differential pressure measurement shall be better than ±0.25 % of the calibrated span.

- Vacuum pressure measurement shall cover the range from 10³  to 10-7  mbar

Vacuum gauges shall be capable of withstanding gas inrush without loss of calibration or mechanical damage.

Liquid level measurements

The Contractor shall measure the liquid-helium level in the QRB using either differential-pressure (qualified for cryogenic service) or superconducting level sensors.

The design, placement and operation of liquid-level sensors shall ensure that their readings are not influenced by:

- bubbles generated by electrical heaters; or

- flow turbulence or other hydraulic disturbances inside the vessel.

Liquid-level readings shall be displayed to operators as a percentage of the nominal working volume.

- The indicated value (including repeatability, hysteresis, and calibration drift) shall be accurate to:

- ± 2 percentage points of full scale for liquid helium; and

- ± 5 percentage points of full scale for all other cryogenic fluids.

Helium flow rate measurements

The accuracy of helium flow rate measurements at cryogenic temperature shall be better than 5% of the full range.

For helium flow rate measurements at room temperature the accuracy required shall be better than 2% of the calibrated span.

Helium Impurity measurements

Pick-ups and sampling

The location of sampling points shall be provided as part of the Detailed Design

Two dedicated gas analyser shall be installed - one in the compressor room and the second one in the cold box room.

These sampling lines shall be provided with at least a pressure regulator, a proper removable filter element and a manual process isolation valve.  All capillaries used for permanent monitoring shall end at the gas analysis.

Temporary sampling points shall be equipped with at least a manual process isolation valve and a plug.

Each gas analyser shall be equipped with a dedicated calibration line.

The analysed gas samples shall be sent back to the Low Pressure  Line of the WCS (WCS-LP)

Gas analysis requirements

The Contractor shall implement continuous measurement of moisture and nitrogen content in the helium gas stream with the following performance:

- measurement range of 0–100 ppm by volume for both moisture and nitrogen.

- measurement accuracy better than or equal to ±1 ppm by volume across the entire range.

- Long-term drift shall not exceed ±1 ppm by volume per year.

The Contractor shall implement a residual hydrocarbons measurement in the compressor room,

The gas analyser shall trigger alarms on the QPLANT:CIS in the event of any anomaly or deviation from specified thresholds.

Welding

The Contractor shall comply with the following requirements:

- All welds shall be completed by welders who are certified in accordance with EN ISO 9606-1 and/or EN ISO 14732 (latest edition) or equivalent.

- All operating modes for each type of welding shall be qualified in accordance with EN ISO 15614-1, or equivalent.

- The staff carrying out the non-destructive testing shall be qualified in accordance with ISO 9712, level 2, industrial sectors.

- The welding procedures shall comply to EN 15614-1(/A1, and /A2)

All permanent junctions shall be welded.  Brazing is permitted only in exceptional cases and subject to prior approval by SCK CEN.

All junctions separating helium and water circuits shall be welded with the weld located on the water side.

Weld inspections

The Contractor shall inspect all welds in compliance with the applicable standards.  To this end, the Contractor shall:

- Perform radiographic inspections for bulk defects in accordance with EN 17636 and EN 25817 (where applicable).

- Perform visual inspections.

- Perform endoscopic (visual) inspections on all hidden welds, including but not limited to butt welds, inner welds, and welds in cryogenic piping.

The weld examinations shall include, at minimum:

- 100% of the longitudinal welds.

- 100% of the T-junctions.

- 25% of the circular welds (per welder, evenly distributed over the circular welds performed by that welder).

- The Contractor shall:

- Indicate in the Manufacturing File which circular welds are selected for inspection.

- Provide the results of the welding inspections to SCK CEN within one week after completion.

The Contractor shall provide associated valid certificates of the qualified personnel for any on-site welding

Certified personnel shall conduct the weld inspections, pressure, and leaks tests.

For tests of weld that are performed on-site,

- radiography with degree of inspection as required by the applicable codes.

Machine Protection

The QPLANT shall protect itself against/minimize damage as far as reasonably possible.  The Contractor shall perform a risk analysis  (e.g. HAZOP, FMECA, or equivalent methodology) and implement all required mitigation measures.  This shall include but not limited to:

  - QPLANT external interfaces

    - Loss of utility (e.g. electricity, water, compressed air, …)

    - Faulty/missing interface to the MCS

    - Operation of the users outside the nominal interface parameters

  - Operator error

  - Any QPLANT internal failure e.g. loss of vacuum, QPLANT trip

The recovery header (QRB.S) shall be protected against over pressures by safety devices and non-return valves.

General Electrical Requirements

All electrical components (including cables, cabinets, cable trays, and associated systems) shall comply with the applicable international electrical standards, including but not limited to IEC 61508 and IEC 61511 for lifecycle functional safety aspects, and [AD 6].

The selection of cable sheathing materials shall explicitly consider and be validated against the environmental conditions to which they will be exposed, including moisture, oil, cable trenches, heat and freezing temperatures, and electromagnetic interference (EMI) effects.

Each electrical and instrumentation cabinet shall provide at least 25% of its internal volume as free space to accommodate future installation of equipment, cabling, or modifications without necessitating structural change.

The Contractor shall install harmonic filtering devices on all major variable frequency drives (VFDs) (e.g., LP and HP compressors), in accordance with [AD 6] and the requirements of IEC 61800-3 for industrial electromagnetic environments.

- The Contractor shall ensure that emission and immunity limits are met through appropriate use of input line filters, output dv/dt filters (where applicable), and proper shielding, grounding, and cable routing practices.

The Contractor shall ensure that all VFD-driven motors operate within the allowable continuous frequency range defined by IEC 60034 (Rotating Electrical Machines).  Nominal VFD operation shall not exceed 60 Hz, unless the Contractor provides substantiated evidence demonstrating that:

- The selected motor and compressor system are rated for sustained operation above 60 Hz.

- The expected Mean Time Between Failures (MTBF) at the proposed operating frequency is documented and acceptable.

- All required mitigations are in place (e.g., output filtering, derating, bearing protection, insulation class suitability).

QPLANT Control System

Overview

The QPLANT Control System (QPLANT:CIS) is the dedicated system for the control of the QPLANT, ensuring all on-site cryogenic processes operate safely and efficiently. 

This IMPLIES that QPLANT needs to provde SCADA (and ‘data_historian’ – trending of historic data, long term storage and backing up. Initiating, source or recovery of data, and validation of expected values or signals


 To function within the wider facility, the QPLANT:CIS is connected with the MCS, the MIT platform, and the MIS. In a later stage, SCK CEN may decide to integrate the QPLANT:SCADA into MCS.

The connection to the MCS is designed to:

Exchange all necessary data between the QPLANT:CIS and the QCELLs.

The integration with the MIT platform is designed to:

Connect to centralized networking

Utilize centralized infrastructure like data storage, backups, and user authentication.

Within the overall machine safety framework, the QPLANT:CIS has a clearly defined role:

It manages the dedicated local protection of the QPLANT, executing immediate safety functions such as automated shutdowns in response to internal faults.

It defers to the MIS for all global safety functions, particularly when the QPLANT interacts with other facility systems

USER_REQUIREMENT for CONTROL_SYSTEM – operator, technician, technical expert (cryogenic engineer, owner, user, RISK, Opportunity, INTERFACES

Reference Architecture

Figure 9 illustrates the reference architecture of the complete cryogenic control system, identifying the QPLANT:CIS as a key sub-system.

Figure 9  Reference Architecture of the Cryogenic Control System

Refer to §8.2.2 for detailed signal and interface mapping shown in Figure 9

Architecture, Autonomy, and Scope

The QPLANT:CIS shall include all components identified in green within Figure 9 (Reference Architecture).  The QPLANT:CIS  shall include any additional systems or subsystems required to meet overall cryogenic system performance, functional, and safety objectives.

The QPLANT:CIS shall use a commercially available, industrial-grade control platform with documented lifecycle support and vendor independence.  It shall meet applicable safety, performance, and reliability standards and shall comply with all relevant regulatory frameworks.

The QPLANT:CIS shall enable autonomous operation of the QPLANT across all defined operational scenarios and transitions, without requiring operator intervention.

The QPLANT:CIS shall support real-time monitoring of instrument health (e.g.: drift, dropout, deviation from expected range) with alarms and diagnostic flags for early fault detection.

Network

Reference Architecture

Figure 10 MIT Reference Architecture

From Figure 10 above, the hierarchy and levels are shown:

Enterprise Network: Represents the high-level IT network connecting various business operations, services, and systems.  It serves as the foundation for communication across the organization.

Industrial Network: Focuses on the network responsible for managing industrial operations and controls, connecting systems such as SCADA, PLCs, and field devices.  It ensures reliable data transmission for production and automation processes.

Plant: This is the central infrastructure that interconnects different network segments, providing high-speed data transfer and ensuring scalability and reliability.

Zone: Acts as an intermediary between the cell and the industrial network, handling traffic distribution and optimizing data flow.

General

The Contractor shall supply a detailed list of the network ports and protocols necessary for the correct functionality of their system and application.)

The Contractor shall be responsible for configuring the necessary network elements based on the inventory of network ports, protocols, internal and external applications.

The Contractor shall use IP address ranges for the QPLANT:CIS as provided by the customer.  This includes equipment in Level 0 of the Perdue model.  These ranges will be pre-assigned by MIT to ensure consistency with the overall network architecture and addressing schemes.

- The Contractor is responsible for implementing the provided IP ranges without deviation, and any additional IP requirements shall be communicated to and approved by MIT prior to implementation.

- The Contractor shall document the use of the assigned IP ranges for each device and submit this documentation to MIT upon completing the configuration.  MIT reserves the right to audit the Contractor's implementation to ensure adherence to the assigned IP ranges and network configuration standards.

Where a Software Component can be upgraded, the QPLANT:CIS shall support an upgrade procedure which can be automated as script(s), without the need for an Internet connection.  A list of required tools must be provided.

Services

Where backup of a system is required, the Contractor shall define (in [DD-8]):

- a clear list of all folders, files, databases, ... that are to be included in a backup

- a document describing the backup and restore process

- any script(s) required to perform these backups and restore actions

Where the system has an operating system, the System shall support monitoring by at least one of the protocols mentioned in the MIT interface catalogue chapter "Monitoring" [AD 23].

Where the system has no operating system and requires authorization, the System shall support authorization by at least one of the protocols mentioned in the MIT interface catalogue chapter "Authorization and security".  [AD 23]

Where the System has an operating system, the System shall support authorization by at least one of the protocols mentioned in the MIT interface catalogue chapter "Authorization and security" [AD 23].

Where the system has no operating system and requires authentication, the System shall support authentication by at least one of the protocols mentioned in the MIT interface catalogue chapter "Authentication"[AD 23] .

Where the System has an operating system which requires authentication, the System shall support authentication by at least one of the protocols mentioned in the MIT interface catalogue chapter "Authentication"[AD 23].

The System shall support network addressing service by at least one of the protocols mentioned in the MIT interface catalogue chapter "Network addressing service"[AD 23].

The System shall support network naming service by at least one of the protocols mentioned in the MIT interface catalogue chapter "Network naming service"[AD 23].

The Contractor shall implement a mechanism for automatic IP address assignment based on MAC addresses whenever possible, utilizing DHCP services to ensure efficient and consistent configuration.  In scenarios where DHCP is not feasible, the Contractor shall configure static IP addresses in accordance with MIT's assigned IP ranges.  All configurations shall align with MIT's network architecture standards to ensure seamless integration and avoid IP conflicts.

The Contractor shall provide a comprehensive list of all devices, including their respective MAC addresses, prior to configuring the network.  This list is crucial for tracking and managing devices, especially when configuring static IP addresses or ensuring proper DHCP assignment.

If a device is DHCP-capable but not configured for DHCP, the Contractor shall provide a detailed procedure for enabling and configuring DHCP on the device.  The procedure shall include all necessary steps for ensuring proper DHCP functionality, such as network settings, IP lease time configuration, and alignment with MIT’s DHCP service and network standards.

Infrastructure

An aggregation network ensures high reliability and performance by implementing redundancy to minimize downtime and enable fast recovery during faults.  Redundant connections ensure continuous backbone network availability by enabling quick failover during link failures, minimizing disruptions, and maintaining system stability.

The aggregation network shall use a redundant ring topology, with a dedicated redundancy manager and client switches.  The network shall automatically reconfigure within 300 ms in case of interruptions.  Redundant connections to the backbone shall be established using a master/slave configuration, ensuring failover times under 300 ms.  All links within the aggregation network, including connections to the backbone and cell networks, shall support 1 Gbit/s bandwidth.  The network design shall incorporate fault recovery mechanisms to reroute traffic in the event of failures, ensuring uninterrupted data flow.

The QPLANT:CIS shall establish redundant connections to the backbone network using standby redundancy.  Each connection shall include a master and backup device, with failover mechanisms ensuring that if one device or connection fails, the other takes over seamlessly.  The failover time shall be deterministic, with a maximum duration of 300 ms to minimize downtime.

Security

The Contractor shall comply with the SCK CEN cybersecurity policy, ensuring alignment with the IAEA NSS17 (Nuclear Security Series), ISO 27001 (Information Security Management), and IEC 62443 (Industrial Communication Networks – Network and System Security) standards.  This includes implementing required security controls, risk management processes, and incident response protocols as outlined by these frameworks.

Documentation of the system's security features and their alignment with the client's standards must be provided for review and approval before deployment.

The Contractor shall work with the client to verify that the system integrates seamlessly with the client’s existing security infrastructure, including firewalls, VPNs, and any other relevant security tools.

The Contractor shall identify all products and digital elements used in the production plant, including Commercial Off-The-Shelf (COTS) materials and custom-built systems, that fall under the scope of the Cyber Resilience Act.  These products must be evaluated for compliance with the CRA's cybersecurity requirements.

If the Contractor requires remote access to the plant, he shall utilize the standard solution provided by the customer.  Access will be granted with restricted permissions to ensure that only necessary functions are available, safeguarding the integrity and security of the plant's systems.  The Contractor is responsible for adhering to the defined access protocols and ensuring compliance with the customer's security policies.

Software Change Management

Prior to deployment in the production environment, software updates shall be rigorously tested in a staging environment.  This minimizes risks of integration issues with MCS, MIT, MIS, or any interfacing systems and downtime of the QPLANT.

Figure 11 Software Change Management

The Contractor shall use a dedicated test environment that replicates the production system's configuration, functionality, and critical interfaces for software changes.  This environment may be virtual, physical or a combination.

The test environment shall mirror the production system to a level that allows reliable validation of all changes under simulated real-world conditions, including performance, response time and stress scenarios.

All changes shall undergo rigorous functional, integration, and regression testing in the staging environment before deployment to the production system.

No changes shall be implemented on the production system without prior approval based on documented test results and validation in the test environment.

The Contractor shall provide a pre-tested rollback plan to ensure the system can be restored promptly to its previous state in case of issues.

All changes shall be tracked in a version control system with an audit trail, providing clear documentation of modifications and approvals.

Changes shall be designed and tested to ensure minimal impact on system availability during deployment, including options for hot-swapping or scheduled maintenance windows.

The Contractor shall guarantee that all testing activities in the staging environment remain completely isolated from production operations to prevent any unintended disruptions.

All regulatory requirements applicable to the delivery of the plant shall also be adhered to for any changes made after delivery, ensuring compliance with safety, environmental, and industry standards.

The contracting authority reserves the right to audit the testing process, staging environment, and changes at any time to ensure adherence to requirements.

The Contractor shall collaborate with stakeholders to evaluate and improve the testing and change management process based on operational feedback and lessons learned.

The Change management should be in place after Factory Acceptance Test and used for changes needed to integrate the consumers.

Test System for Functional Verification

The Contractor shall deliver a dedicated, fit-for-purpose Test System for functional testing, validation, and commissioning of the System Under Test (SUT), specifically the QPLANT and its QPLANT:CIS

The Test System shall emulate key operational states including normal start-up, shutdown, transients, degraded modes, and fallback conditions.

The Test System shall enable alarm logic verification, interlock testing, and diagnostic evaluation without reliance on the live operational system.

In the Offer, the Applicant shall:

- Describe proposed SUT/Test System architecture.

Digital Process Model

A complete digital process model (transient simulation or digital twin) is not mandatory.  However, if the Contractor proposes one, the following requirements shall apply:

Any proposed model shall use certified, validated, or standards-compliant toolsets (e.g., Simulink®, SimCryogenics, or validated statistical/ML models).

The model shall support operator training, failure simulation, diagnostics, and maintenance planning.

The model shall enable future integration into the control system to support virtual sensors, inference algorithms, and predictive diagnostics.

In the Offer, the Applicant shall:

- State if they will provide a digital process model and motivate it the decision by a cost-benefit analysis.

- If it is not provided, the Applicant shall describe alternative approach for commissioning, fault simulation, diagnostics, training.

Cryogenic System Control and MCS Integration

The QPLANT:CIS shall regulate the mass flow rate and supply temperature at the QRB-DIST interface ensuring that the temperature change rate (during cool-down and warm-up) for QCELL during transients remains within predefined limits and the operational window.  The temperature change rate is defined as the maximum allowable rate of change of the internal QCELL temperature, expressed in K/h (e.g., 4 K/h).

The QPLANT:CIS shall allow the adjustment of these limits, the global cooling/heating rate during operation.

The QPLANT:CIS shall support bidirectional communication with the Concentrator PLC (refer to Figure 9 and items 20 and 33), exchanging real-time operational and control signals at an update rate of 1 Hz.  This will be used by the Concentrator PLC, implemented within MCS, to actively control and enforce this temperature change rate by issuing setpoints to the QPLANT.

The QPLANT:CIS shall route all control commands, system status updates, and alerts related to cryogenic operation via MIT to ensure centralized visibility and unified supervision across QPLANT and QCELL domains.

General Software and Hardware Requirements

The Contractor shall follow the applicable sections from the General Software and Hardware Requirements for Contractors (GSHRC) containing quality and other requirements related to software, firmware, and interoperability as per

When the MCS is unavailable or a communication loss occurs, the QPLANT:CIS shall continue to operate as long as the systems safety as well as personnel safety are guaranteed.

All the control parameters relevant for User Integration and monitoring (e.g.: setpoints and thresholds), including calibration data  shall be available to the remote-control interface with MCS.

Interlock thresholds shall not be writable through the remote-control interface.

The QPLANT:CIS should allow every actuator to be controlled manually in the event of a malfunction (for example a motor can have an auto, manual override to fixed values).

In maintenance mode, the QPLANT:CIS shall allow every sensor value to be set by the operator to be interpreted by the QPLANT:CIS as it is the real value coming from the sensor.

Records of all measured values, valve positions, operator actions, logbook and alarms shall be accessible in QPLANT:CIS.

Software development

The Contractor shall provide the following as part of Control System Dossier [DD-8]:

- The detailed documentation of the software architecture, covering all modules, functional blocks, and components, along with their inputs and outputs.

- lists of alarms, protection functions, instruments, events, and parameters.

In the offer, the Applicant shall provide sufficient detail deemed representative of the anticipated software development scope, including assumptions, planned methodologies, and architectural breakdown.

All PLCs shall be programmed in full compliance with the IEC 61131-3 standard.

- The use of Instruction List (IL) is highly discouraged.  Higher-level languages like Structured Text (ST) are highly recommended for better clarity, maintainability, and portability of PLC programs.  Therefore, users and developers are strongly advised to avoid new implementations in IL and to migrate any existing IL-based code to ST, GRAFCET and FBD or other recommended IEC 61131-3 languages whenever possible.

In the offer, the Applicant shall:

- Declare the programming languages to be used per functional block.

- Justify any deviation from ST, GRAFCET and FBD, including retained IL-based implementations.

- Demonstrate software structuring practices that favour maintainability, reuse, and modular design.

Proposals will be evaluated with preference given to Applicants demonstrating disciplined use of structured IEC 61131-3 languages and long-term maintainability strategies.

When the Software Component includes human readable information (for example, but not limited to: HMI, logging, source code), it shall be in English.

The Contractor shall develop a functional analysis and a detailed description of all control scenarios including interfaces.  The detailed description shall also include a program sequence plan (functions and procedures used in the program).  For each software module, functional block, component, or data block, the Contractor shall provide a detailed description of the logical conditions and input states that govern the activation, value assignment, or change of each output parameter.

In the offer, the applicant shall provide a preliminary functional analysis and indicative control sequence plan, representative of the anticipated implementation.  This shall include key functions, procedural steps, and interface interactions necessary to support evaluation of scope, architecture complexity, and design maturity.

Each Software Component and Hardware Node shall include a unique version identifier that uniquely represents the build date and Git commit hash, automatically generated during the build process to ensure traceability; this identifier shall be retrievable in a consistent and read-only manner through the MCS control and monitoring interface.

Human Machine Interface (HMI)

The Contractor shall deliver local operator stations to provide local data collection and reporting for the QPLANT system to support maintenance activities.  As a minimum one is expected in the Compressor Room and one in the Cold Box Room.

The Contractor shall not deliver or implement an enterprise level QPLANT SCADA system (multi-user or multi-server architecture) as part of the scope.

The Contractor shall deliver and implement a temporary QPLANT SCADA system exclusively for use during the standalone commissioning phase.  This solution is intended solely to support initial testing, commissioning, and operator training, and should be decommissioned and replaced by the MCS solution once integration is realized.  This temporary system shall also be used as reference design for the development of the MCS Navigator therefor sufficient documentation is required.

The Contractor shall provide support for integration of the QPLANT:CIS with the MCS Navigator.  This includes, but is not limited to:

Providing support in designing the Operator Screen for the Plant.

Supplying necessary communication protocols (e.g., OPC UA, TCP/IP)

Coordinating with the project SCADA team to ensure data consistency (e.g., tags, alarms)

Sharing relevant technical documentation and engineering details to enable seamless integration

The Contractor shall ensure that the operator stations (whether HMI panels or dedicated Industrial touch PCs) are based on industrial-grade hardware specifically designed for continuous operation in a production environment.  This includes robust construction, compatibility with the QPLANT’s environmental conditions (temperature, dust, vibrations, ...), and adherence to relevant industrial standards.

The platform shall be supported with software updates, firmware updates, and security patches for a minimum of 20 years from the date of commissioning.  The Contractor shall provide documentation or official manufacturer statements guaranteeing availability of updates throughout this period.

In the offer, the Applicant shall explicitly address the obsolescence management strategy for the proposed PLC or control system platform, considering the anticipated forty (40) year operational lifetime of QPLANT.  This shall include:

- Manufacturer support lifecycle documentation

- Spare part availability forecasts and migration plans

- Platform evolution roadmap (e.g., upgrade compatibility or virtualization strategy)

- Technical or commercial approach to sustaining software and hardware support beyond the guaranteed 20-year update period (e.g., stockpiling, long-term service contracts, emulation layers).

Migration to Newer Hardware

The visualization (HMI) project shall be designed in such a way that it can be migrated to newer hardware of the same manufacturer if the originally delivered hardware becomes obsolete or requires upgrade.  This includes ensuring future compatibility of project files and software licenses and providing guidelines for seamless transfer of project data and configurations.

Where the system includes a local Human Machine Interface (HMI) that supports local control, it shall implement a control selection mechanism based on a 3-state principle: Local - Free - Remote.

- Local or remote control can only be granted when the system is in the ‘free’ state.  If the system is not free, the requester will be denied the requested control, and any write commands from that side will be ignored.  However, reading the system state shall always be permitted in any state, allowing either side to retrieve information about the system's status and confirming whether a request was successful.  Writing (changing) is only allowed when the request is accepted.

- This control mechanism only pertains to local versus remote control states.  Any other state machines within the system shall remain active, ensuring that, for example, regulation loops continue to function in either state.

Once a system is reserved in a specific control mode, it shall automatically transition to the "Free" state if a configurable timeout period (maximum of 5 minutes) of non-activity expires.  "Releasing" means transitioning from a specific control state to the "Free" state.  Non-activity refers to the absence of local or remote actions.

The Operator Station shall be designed as a non-critical component of the control system.  No real-time or safety-critical control functions shall reside in the Operator Station; it is purely for monitoring, visualization, and local interaction.

The Operator Station shall store operational data (e.g., trends, alarms) only for a limited amount of time, sufficient for short-term analysis and troubleshooting.  The data stored locally shall not be formally backed up; once data ages out of the configured retention period, it may be overwritten or discarded.

The Operator Station shall provide capabilities for plotting curves and trends, enabling real-time and short-term historical visualization of key process variables.

The Operator Station shall include graphical process views, providing an intuitive interface for monitoring equipment states and process flows.

The Operator Station shall show and log alarms and events for immediate operator awareness without functionality to acknowledge alarm occurrences

Graphical process views shall be agreed with SCK CEN as part of [DD-8]

All the sensors and actuators shall be integrated in different graphical views.

The Operator Station (PLC with IO mirroring QPLANT:CIS (PLC in WCS and PLC in QRB)) software shall support a default data acquisition period of maximum two seconds.  For critical turbine data an acquisition rate of 100 ms is required.

The HMI software shall allow at least two permission levels with distinct functions available.

The QPLANT:CIS shall allow to automatically call or e-mail “on call” staff through MIT

The graphical views shall be in accordance with the Process & Instrumentation Diagrams to easily understand and operate the system.

The HMI software package shall be installed on two workstations with large screens (at least 24 inches diagonally monitors) to visualize the useful information during QPLANT operation

Interfaces

or the event of a Loss of Offsite Power (LOOP) to the MINERVA facility, the Contractor shall assume the following utilities are available after a short interruption (few minutes):

- Up to 350 kW of back-up power (supplied by a diesel generator)

- Up to 350 kW of back-up cooling water.

The emergency cooling-water header is hydraulically common with the normal WCS cooling-water header but may operate at reduced total flow under emergency conditions.

The technical interface details of these backup systems shall be co-developed between the Contractor and SCK CEN during the Concept Design Phase and fully defined and documented by the Contractor.

- Electrical Integration (Emergency Diesel Generator Interface)

  - The Contractor shall define the voltage level and switchboard configuration to which the diesel generator supplies power.

  - The Contractor shall specify the feeder cable rating, breaker and fuse characteristics, and the applicable earthing scheme in accordance with IEC and local electrical standards.

  - The Contractor shall confirm whether the emergency bus shall be radially fed, or whether it shall require an Automatic Transfer Switch with appropriate synchronization capability to re-establish supply post-LOOP.

- Cooling Water Provisioning

  - The Contractor shall define the operating pressure, temperature, and flow rate of the cooling water available under generator-backed emergency operation.

  - b) The Contractor shall propose the tie-in point, including line size, and shall confirm whether non-return valves or back-pressure controls are required to ensure stable flow during switchover.

In the offer, the Applicant shall provide an enveloping preliminary design for the configuration, internal routing, and management of abnormal utility supplies (electrical and cooling-water) during a Loss of Offsite Power (LOOP) event.  This shall include:

- A functional description of the proposed emergency bus and emergency cooling-water header

- A list of critical loads expected to be maintained under LOOP conditions

- Enveloping assumptions for internal distribution logic, including switching, prioritization, and load control schemes

- Proposed interface boundary conditions with SCK CEN’s emergency diesel generator and cooling-water header

Process Line interface

With reference to Table 11 and Table 12 the following applies:

The Contractor shall size and install QRB.A for SHe flows ≥ 50 g s⁻¹ at 3 bar(a) and T ≤ 4.5 K, including insulation, supports, and P&ID tagging.

The Contractor shall size and install QRB.S to accept up to 200 g s⁻¹ of warm helium to the VLP header under emergency vent conditions, meeting PED over-pressure rules.

The Contractor shall route WCS.HP/LP/VLP headers through designated wall sleeves, providing expansion compensation and removable spools for maintenance access.

The contractor shall finalize clear enveloping terminal point design and flow conditions (as per ICD) by no later than the end of L1 – Conceptual design (details contained in ICD, and . Current sizing/flowrate indicative of scale (~81 g/s for QDIST.D/E is based on dT=20 K of QDIST and QCELL Sizing values in this matrix are enveloping and indicative.

Thee supply pressure of QRB.D (at present 13 bar, may be reduced if temperature of supply not doable at that pressure.

- Note: The current BSL constitutes a conservative ‘available pressure’ to ‘remove’ any pressure drop for TS out of the QCELL design considerations.

In the offer the applicant shall clearly state the highest pressure of delivery.  A pressure drop of 1 bar over the total system (~300 m including the TS-payload).

In the offer the Applicant shall confirm exact mass-flow, pressure, and diameter and detail them in the Conceptual Design.

Table 11  Interface ID between QRB and QDIST  (cold interfaces)

| Line ID | Purpose / Duty | Design Flow rate | Operating Envelope | Notes |
| --- | --- | --- | --- | --- |
| QRB.A | Supply of super-critical He (SHE) at 4.5 K to QCELL distribution | 50 g s⁻¹ | 3 bar(a), ≤ 4.5 K | Cold helium to cryomodules |
| QRB.B | 2 K return / suction from QCELLs | 50 g s⁻¹ | ≤ 27 mbar(a), 2 K | Managed by QRB cold compressor |
| QRB.D | Thermal-shield supply | 85 g s⁻¹ | ~14 bar(a), 40 K, | Matches return flow of E |
| QRB.E | Thermal-shield return | 85 g s⁻¹ | ~13 bar(a), 60 K, | Returns to QRB |

The QPLANT shall interface to the QLM at the cold end of the QRB.  The QPLANT shall contain the final vacuum barrier and the isolation cryogenic valves.

The QLM contains the following cryogenic lines:

        - “A”: Supply of supercritical helium.

        - “B”: Return of very low pressure helium.

        - “D”: Supply of gaseous helium to the TS.

        - “E”: Return of gaseous helium from the TS.

Figure 12 Preliminary arrangement of the pipes in the QLM - 
see Table 12 for details

A preliminary arrangement of the distribution headers in the QDIST is shown in Figure 12.  The preliminary diameters of the pipes are indicated in Table 12.  The final arrangement and pipe diameters shall be defined by SCK CEN in due time.

Table 12 Preliminary pipe diameters for the QLM

| Line/Pipe | DN (mm) | External diameter (mm) | Thickness (mm) | Indicative operating pressure (bar) |
| --- | --- | --- | --- | --- |
| A | 25 | 33.4 | 1.65 | ≥ 3 |
| B | 150 | 168.3 | 2.77 | ~0.03 |
| D | 40 | 48.26 | 1.65 | ~14 |
| E | 40 | 48.26 | 1.65 | ~13 |
| Thermal shield |  | ~350 | 3* | - |
| Vacuum jacket |  | ~500 | 4.5 | 10-6 |

The welding connection between QRB and QLM shall be done by SCK CEN.

For the acceptance tests, the Contractor shall provide the necessary welded caps on pipes on the QRB side.

Table 13  Interface ID between QRB and QINFRA  (warm interfaces)

| Line ID | Purpose / Duty | Indicative Flowrate | Operating Envelope | Notes |
| --- | --- | --- | --- | --- |
| QINFRA.U | Warm GHe utility / ad-hoc supply | ~10 g s⁻¹ | ≤ 2 bar(a), 300 K | Occasional user demands |
| QINFRA.W | Warm return from QCELL couplers to VLP stage | ~5 g s⁻¹ (nominal 2 g/s) | ~1 bar(a), 300 K | Coupler (QPLR) exhaust |
| QINFRA.S | Safety vent to VLP compression | Up to 200 g s⁻¹ (Loop event) | 300 K | Emergency discharge path |

QINFRA.U and QINFRA.S are not participating in the cryogenic cycle and nominal cryogenic heat sink demand from the user (QCELL), with QINFRA.W the only warm line with active refrigeration participation that represent the liquefaction load (~4% supply of QRB.A, during nominal 2K Operational Scenario).

Table 14 Internal QPLANT Distribution Lines (crossing multiple rooms)

| Line ID | Purpose/Duty | Indicative Flowrate | Operating Envelope | Notes |
| --- | --- | --- | --- | --- |
| WCS.HP | High-pressure header from warm compressors to QRB | ~350 g s⁻¹ | 15 bar(a) | Insulated hard-pipe, traverses Compressor Room → Cold-box Room |
| WCS.LP | Low-pressure return header to warm compressors | ~300 g s⁻¹ | 1.05 bar(a) | Continuous purge maintains ≥ 1 050 mbar(a) |
| WCS.VLP | Very-low-pressure header VLP compressors | ~50 g s⁻¹) | 0.40–0.55 bar(a) | QRB.B Coldbox passthrough + Receives QINFRA.W and QINFRA.S flows |

In the offer the applicant shall furnish the following deliverables and form part of the Interface Control Document (ICD) and will form technical baseline for offer and Conceptual Design Start (L1 in Project Lifecycle).

  - Terminal-point definition (quantified with)

  - 3-D model representation

- Extract or viewpoint showing each cryoline from first anchor to terminal flange

- Clash-free routing through all penetrations and service corridors

  - Refined mass-flow & diameter table

- Confirmed operating envelope for every line family (pressure, temperature, allowable ΔP)

- Instrument take-off points (PT, TT, FT) and required maintenance clearances (Concept Design Latest)

The following warm lines are distributed in the tunnel.  The interface with the QPLANT will be in the cold box room, around the QRB.  The final location and pipe requirement shall be defined during the design phase with SCK CEN.

- Warm GHe supply (QINFRA.U): This line supplies helium to the cryogenic users (300 K – 14 bar).  It is high pressure (coming from the HP of the compression station), the interface pipe diameter is DN 25.

- Safety Valves GHe recovery (QINFRA.S): to avoid loss of helium and to reduce anoxia risk, the safety devices shall be collected.  The diameter of the pipe is DN 150.

- Coupler return line (QINFRA.W): This line collects the helium gas at the outlet of the coupler cooling circuits (300 K and 1.1 bar).  It shall be connected directly to the LP pressure of warm compressors at 1.05 bar.  The selected diameter of this line is DN 25.

Table 15 Warm lines at room temperature

| Pipe | DN (mm) | External diameter (mm) | Thickness (mm) | Indicative operating pressure (bar) |
| --- | --- | --- | --- | --- |
| Warm GHe supply (U) | 25 | 33.4 | 1.65 | ~ 14 |
| Safety Valves GHe return (S) | 150 | 168.3 | 2.77 | ~ 1.05-1.15 |
| Coupler return line (W) | 25 | 33.4 | 1.65 |  1.1 |

To cope with a return mass flow rate through the safety valves around 100 g/s (case of utility stop for more than 1 hour), the diameter line shall be at least DN 150.

In the LINAC tunnel, a line called “vent collector, Line V” could recover the burst disk of the Cryogenic Cells (QCELL’s) to vent helium outside tunnel in case of major failure.  This vent collector is out of the present scope and does not have any interface with the QPLANT.

Interface with support systems (utilities)

Electrical Interface Provisioning

The SCK CEN site shall provide a dedicated 400 V~, 50 Hz, 3-phase + Neutral (TN-S) electrical supply at the following interface terminal points (dedicated to user location inside WCS):

WCS (Warm Compressor Station, CCB Building):

HP Compressors (four (4) individual)

PVPS (Pressure-Volume Protection System)

ORS Electrical Heater

Analyzer

WCS UPS and Controls

QRB (Cold Box Room, AUB Building):

Cold compressors CC1, CC2, CC3

QRB Controls

QRB Varia (auxiliary loads and other installed systems)

The Contractor shall provide the complete Low Voltage (LV) distribution system for QPLANT, including LV cabinets, switchboards, and protection devices.

The Contractor shall route, install, and connect all electrical cabling, cable trays, and interfaces for the compressor room, cold box room, and warm helium storage area ‘except for the dedicated supply as per above.

All electrical design files—including one-line diagrams, layout plans, and protection studies—shall be submitted for SCK CEN approval.  Grounding interfaces shall be connected to SCK CEN-provided terminals in each area.

The Contractor shall ensure all QPLANT equipment is connected to the respective building grounding network, fully compliant with IEC 60364 and IEC 61000 EMC requirements.

All helium piping, water, air lines, and LV cabling entering each building shall pass through a single shared feedthrough and be connected to equipotential bonding systems to mitigate EMI risks.  EMC best practices and shall apply.

The Contractor shall define the required UPS backup scope and loads (HMI, PLCs, network, digital I/O) to ensure full operational redundancy in the event of utility loss.  SCK CEN will provide central UPS backup infrastructure.

The Contractor shall submit a risk-based signal classification and UPS demand report, listing all sensors, transmitters, and I/O requiring backup, subject to SCK CEN approval to finalize UPS system dimensioning.

Where high voltage (HV) or high-power systems exist, embedded controls shall be powered using a dedicated and segregated low-voltage AC feed.  These feeds shall be galvanically isolated from the HV main circuits.

In the Offer, the Applicant shall:

- Provide the total and per-building load assessments (normal and peak demand) to define final terminal point loads.

- Submit Single Line Diagram (One Line Diagrams) aligned to the ‘spatial split’ (2 rooms in 2 different buildings and terminal point logic described above.

- Include a UPS backup proposal, risk analysis, and critical signal identification.

- Confirm EMC and equipotential bonding compliance per IEC 61000 and AD 7.

- Declare isolation strategies for embedded electronics in HV environments and list any required auxiliary supplies.

Interfaces with the Water-Cooling Loop (NA.PS01.PAB12)

Cooling water (mixture with 40 % of propylene glycol) in the compressor room for the warm compressors and in the cold box room for rotating machines (turbines, cold compressors, pumping system) will be provided by SCK CEN site at one point (supply and return) in each building at the dedicated technical rooms (Compressor Room and Cold Box Room).

The nominal cooling water temperature supply is 27°C (+/- 2°C) with an expected temperature difference around 10°C (Treturn-Tsupply).  The Maximum supply temperature is 29 °C.

Water supply pressure is of 10 bar can be assumed; physiochemical properties are given by:

The Contractor shall assume a maximum supply of cooling water 100 m3/h of 40% glycol.

The Contractor shall provide the cooling water expected consumption at the end of the Conceptual Design phase.

The Contractor shall distribute the cooling water inside the dedicated technical rooms to the different QPLANT users.  The scheme of the cooling water distribution in the buildings shall be subject to approval by SCK CEN.

The Contractor shall install all necessary instrumentation and additional control elements to measure/control temperature, pressure and mass flow rate of the cooling water loops.

The Contractor shall provide local drains considering that the draining of cooling water is a glycol type waste and therefore needs to be connected to the SCK CEN PS03 system.

Interfaces with Instrument Air System (NA.PS05.XXX)

Instrument air in the compressor room and in the cold box room will be provided by SCK CEN site at one point in each of the dedicated technical rooms.  Instrument air pressure will be around 9 bar with a dew point lower than -40 °C.  For the QPLANT, a maximum of 50 Nm3/h of compressed air will be available.

The Contractor shall provide the compressed air needs at the end of the Conceptual Design phase.

The Contractor shall distribute the compressed air inside the dedicated technical rooms to the different QPLANT users.  The scheme of the compressed air distribution shall be submitted to SCK CEN’s approval.

Interfaces with HVAC (NA.HV02/3)

In the offer, the Applicant shall specify the terminal point(s) of the HP compressors to the HVAC system including duct cross-section, air-flow rate, and interface flange type.

The Contractor shall provide a quantitative analysis of heat dissipation to the HVAC system covering:

  - Heat load to (compressor and cold box) room and cooling air (in kW) for steady state (24 and 30 QCELL) operational and standby scenarios.

  - Validation of SCK CEN provided exhaust routing to designated HVAC intake points during commissioning and acceptance testing.

The Contractor shall ensure the integration of the HP compressor exhaust ducting with the Compressor Room HVAC system (WCS in CCB).  SCK CEN provides extraction from defined scope boundary.

The total heat dissipated by the WCS to the surrounding air shall not exceed 120 kW under any steady-state operating condition (including HVAC load from HP compressor ducts).

In the offer, the Applicant shall furnish interface (HP compressor exhaust outlet/terminal points) quantitative data (heat dissipation, flow rates, pressure drop, …)

In the offer, The Applicant shall quantify flow rates, temperatures (maximum, nominal, minimum), and provide outlet dimensions and fixed interface and terminal point definition.  The allowable pressure drop from the compressor to the outside shall be specified.

Heat recovery

The heat produced by the LP/HP compressor is to be partially recovered to supply a heating system only operating when there is a need for hot water.

At least 65 % of the compression power dissipated as heat by the LP and HP compressors shall be recoverable via the site hot water network (40/50°C) described in 3.8.2.4.

- The heat-recovery function shall operate only when a hot-water demand signal is present.

The Contractor shall demonstrate, by heat-balance calculations, that the recovered-water temperature and the percentage of heat recovered meet the 65 % target when the cooling-water supply temperature is 27 °C.

In the offer, the applicant shall quantify the expected heat recovery per operating scenario)

Interfaces with the site

Figure 2 gives an overview of the buildings on site (details are given in [AD1]).  The QCELLs are in the tunnel (LTU).  The QRB is in the cold box room and the WCS in the compressor room (CCB).  A transport distance of ~65 m applies.

The QPLANT shall be designed to meet the site constraints (buildings, rooms) given in AD1.

The Contractor shall provide the general assembly drawings with QPLANT components and 3D models.  (*.step files may be used).

In the offer, The Applicant shall quantify the number, size, and location of expected roof/wall penetrations

Compressor room

The compressor room shall house the WCS.  (ALL equipment via door entrance of 2.5 m)

The Contractor shall define the positioning of all equipment in this room in agreement with SCK CEN.

The compressor units may be installed and grouped on skids.

During the conceptual design phase, the Contractor shall evaluate the need for a crane in the compressor room and shall provide the necessary inputs in Conceptual Design Report (weight and dimensions)

The access for the installation of the large components could take place from the road by removal of the wall dismountable panels.  SCK will oversee the dismountable panels dismounting and mounting.

The cold box room

The Cold Box Room shall host the Refrigerator Cold Box and associated warm panels, the electrical cabinets, the gas analyse and pumping (vacuum) system.  The height of the ceiling is around 6.5 meters.

During the Conceptual Design phase (LCP1), the Contractor shall evaluate the need for crane in the cold box room and shall provide the necessary inputs in the deliverable

The access for the installation of the large components could take place from the road by removal of the wall dismountable panels.  SCK will oversee the dismountable panels dismounting and mounting.

The cold box room shall be connected to the compressor room by the different warm lines of the QPLANT.

These warm lines of about 60 meters long shall be installed on the roof or below the roof close to the ceiling of the buildings between compressor room and cold box room.

- In the offer, the Applicant shall give enveloping coldbox (QRB) dimensions,  lifting mass and clearances and road loads.

Storage Area

The gas helium storages and potentially liquid nitrogen storage shall be installed in the storage area (next to the compressor room.  The total helium inventory is detailed in §3.6.4.

The positioning of the different storages shall consider the possibility of the fluid refilling by trailers.

Site environmental conditions

The following site operating conditions shall be considered for the design and operation of the QPLANT and auxiliary equipment:

- Winter design condition

  - Dry-bulb temperature: −9.1 °C

  - Relative humidity: 90 %

- Summer design condition

  - Dry-bulb temperature: 33.4 °C

  - Relative humidity: 39 %

- Technical-room ambient range

  - Cold-box room temperature: 5 °C – 40 °C (Range may be reduced for specific cold-box components upon Contractor’s request)

  - Compressor room temperature: 5 °C – 40 °C

  - Relative humidity: Not controlled

- Environmental design loads

  - Wind speed: 49 m s⁻¹ (≈ 176 km h⁻¹), 3 s gust at 25 m height (NBN 460)

  - Rainfall: 54 mm in 1 h (100-year return)

  - Snow load: 0.50 kN m⁻² (100-year return)

- Site altitude & coordinates

  - Elevation: 27 m a.s.l.

  - Location: 51° 13′ 50″ N 5° 05′ 24″ E

Interfaces with the Vacuum System

The exhaust of the vacuum system(s) from the QPLANT process rooms shall be collected and vented outside the building.  The location of these exhausts shall be subject to approval by SCK CEN.

The Contractor shall provide the necessary helium to be used during the installation, commissioning phases and acceptance testing including leak tests and conditioning of the QPLANT circuits.

Interface with LHe (ad-hoc) user and associated helium recovery

Recovery and purification system for ad-hoc user

The QPLANT shall include a recovery header for helium gas at room temperature and atmospheric pressure collecting safety valves and potentially for future external user.

Envisaged future external user amounts (future external helium users liquid supply by dewar and gaseous return) will be about 200 litres for initial cooldown and 50 litres/day while the relevant experimental setup is operational).

This recovery header shall be connected to the LP of the warm compressors.

The pressure and mass flow through the recovery header shall be permanently measured.

The possibility to connect in the future to a recovery gas bag and external purification system shall exist.  The Contractor shall make recommendation on required external purification system, or as a minimum specify the limits (in terms of impurities) to avoid negative impact on the main QPLANT function.

General

This section defines the physical and functional interface between the Cryoplant (QPLANT) and an external or ad-hoc user consuming liquid helium (LHe) and returning gaseous helium (GHe) to the plant recovery network.  The interface is located at QRB.EUR (External User Recovery).

The objective of this interface is to enable safe withdrawal of LHe for experimental use while ensuring that all boil-off helium is recovered under controlled pressure, maintaining gas purity and system stability.

Functional Description

The external user shall withdraw liquid helium from a 500 L user-owned Dewar, transferring it in batch mode to the experiment.  The helium boiled off from the experiment shall be routed back to the QPLANT recovery network via the dedicated LP return header (QRB.LP).

Typical operating parameters:

Table 16 External Helium User Quantification

| Condition | Liquid He | Equivalent Gas | Return Rate | Notes |
| --- | --- | --- | --- | --- |
| Cooldown (startup) | 200 L | ≈ 149 Nm³ | ≈ 0.31 g/s | one-time, short duration |
| Steady operation (typical) | 50 L / day | ≈ 37 Nm³ / day | ≈ 0.08 g/s | continuous boil-off |
| High transient (3 × normal) | ≈ 150 Nm³ / day | ≈ 0.24 g/s | representative upset | Representative upset |

For a 30-day campaign (1 per calendar year), total returned helium ≈ 1 100 – 1 200 Nm³, equivalent to ≈ 200 kg He.

Return pressure: maintained ≥ 1.00 bar(a), nominal 1.05 bar(a).

Helium purity for acceptance: O₂ ≤ 1 ppm, N₂ ≤ 5 ppm, dew point ≤ –80 °C.

SCK CEN is fully responsible for Dewar logistics, batch filling, and maintaining helium purity

QPLANT shall accept helium gas into the recovery network only when purity is within specification.  If gas analysis indicates contamination above limits, the recovery valve shall remain closed, and helium shall be vented at the user side.

- No purification or gas clean-up by QPLANT is foreseen for this interface.

Figure 13 Routing of QRB.EUR (External User Recovery)

The Contractor shall provide a complete interface assembly at QRB.EUR consisting of a check valve, automated isolation valve, removable end cap, and gas-sampling take-off.  All components shall be helium-tight and suitable for room temperature helium.

The external-user return circuit shall maintain stable suction pressure and flow during all operating conditions.
The Contractor shall design the return line to maintain 1.05 bar(a) ± 0.02 bar(a) for helium gas flows of 0.06 – 0.08 g/s (steady) and up to 0.30 g/s for short-term transients.  Pressure stability and flow compliance shall be verified by continuous logging during commissioning.

Safe isolation and purge capability shall be ensured for all operational and maintenance modes.
The Contractor shall install remotely operated emergency shut-off valves (ESD) on both the liquid-helium supply and gas-return lines, closing within 5 s of an emergency signal.  Manual vent/purge ports shall be provided to allow drying and safe warm-up of the interface and user line.

Helium recovery shall only occur when the returned gas purity is within specification.
QPLANT shall accept gaseous helium only when purity meets O₂ ≤ 1 ppm and N₂ ≤ 5 ppm.

The Contractor shall integrate an oxygen and dew-point analyser at QRB.EUR to verify compliance and prevent any process contamination.  If the gas is out of specification, the recovery valve shall remain closed, and the helium shall be vented on the user side.

Liquid Nitrogen (LN2)

If liquid nitrogen is used for the QPLANT precooling, the Contractor shall be responsible for the entire nitrogen equipment including liquid nitrogen tanks, heaters, ….  If the liquid nitrogen is not used for the QPLANT precooling, SCK CEN shall provide gas helium for regeneration purpose.

During installation and commissioning, the Contractor shall be in charge to supply the necessary nitrogen linked to these activities.

Interfaces with (external) Control System

Interfaces with MCS

Where the system has an interface with MCS, the system shall comply to the MCS architecture, processes, and interfaces.  [AD 18]

The interface between QPLANT (Contractor) and Control System (ICS) shall comply to the Slow Fieldbus Control and Monitoring Interfaces type C as listed in MCS Interface Catalogue [AD 20].

Interfaces with MIS

Where the system has an interface with MIS, the system shall comply to the MIS architecture, processes, and interfaces  [AD 19]

The interface between QPLANT (Contractor) and Interlock System (ICS) shall comply to the Slow control interface catalogue [AD 22]

Where the system has a slow interlock interface, the slow interlock interface shall comply to the slow interlock interface document: Interfaces with MIT [AD 23]

Where the system has an interface with MIT, the system shall comply to the MIT architecture, processes, and interfaces.  [AD 19]

The interface between QPLANT (Contractor) and SCK CEN Information Technology (ICS) shall comply to the MIT interfaces as listed in catalogue  [AD 23]

The QPLANT shall be physically connected to the MIT network in a redundant, fault tolerant way.  At minimum 2 physical links will be foreseen, each link routed via a separate pathway.  The physical connections need to be distributed over at minimum 2 separate physical endpoints on the QPLANT side.

The QPLANT shall be connected to the MIT IP network using a single logical routed connection ("layer 3").  At both sides, a single gateway IP will be configured as destination IP for packet forwarding.

Where the QPLANT:CIS or one of its components supports system logging, the contractor shall provide system logs remotely through at least one of the protocols mentioned in the MIT interface catalogue chapter "System logging".

Where the QPLANT:CIS support application logging, the System shall log remotely either by using a protocol defined in section "Application logging" of document "MIT interface catalogue") or alternatively adhere to the following:

- Logs are provided in a data and file format that is machine readable, text based and non-proprietary.  Examples of this include but are not limited to: CSV (Comma Separated Values), JSON (JavaScript Object Notation), GELF (Graylog Extended Log Format) or “Common Log Format.”

- The details of the used log format(s) are provided.  This includes but is not limited to the message structure and the possible key/value pairs with their type, value, and description.

- Logs can be encrypted during transport if the security classification of the data permits this, but in this case the decryption procedure and required secret(s) need to be provided.

The QPLANT:CIS shall support timing synchronization by at least one of the protocols mentioned in the MIT interface catalogue chapter "Timing synchronization".

Where the QPLANT:CIS requires remote access; Systems shall provide remote access through at least one of the protocols listed in the MIT interface catalogue chapter "Remote access".

The connection of the QPLANT:CIS with MIT, shall terminate on a patch panel.

Verification and Validation

All measurement and testing instrumentation used at the performance of the Contract shall have the appropriate qualifications and shall be regularly calibrated to ensure appropriate accuracy and precision for the measurement at hand.  SCK CEN reserves the right to request a measurement system analysis and/or proof of calibration in case of any doubt of appropriateness.

In the offer, the Applicant shall outline the quality control process that shall be implemented during Contract execution.

- Quality assurance Program

Prior to beginning any work from L1 (Conceptual Design), the Contractor shall submit a detailed Quality Assurance Program, QAP, for review and approval by SCK CEN demonstrating compliance with the QA/QC requirements set out in this document.  The Contractor and all its Subcontractors shall adhere to the QAP and shall apply the mandatory QA/QC measures to each deliverable.  Any required change to the QAP during Contract execution shall be requested from SCK CEN via a Change request.

In the offer, the Applicant shall include a preliminary version of this QAP.

Manufacturing and Inspection Plan

The Contractor shall prepare a Manufacturing and Inspection Plan (MIP) covering all tests and inspections from start of manufacturing to provisional acceptance.  It shall, as a minimum, include test and inspection plans & procedures and (if on-site at SCK CEN) utilities necessary for executing the tests.

- It shall define, for each subsystem and activity, the applicable codes and standards, inspection and test methods, acceptance criteria, documentation to be produced, and the responsible or witnessing party, including any notified bodies where applicable.

- It shall indicate the Hold Points and Witness Points defined in the Contract as well as any other HP/WP defined by SCK CEN during execution of the Contract.

  - The MIP shall serve to verify that all tests and inspections are executed as planned and in compliance with the agreed HP/WP.

- A preliminary version of the MIP shall be provided during L2 in DD-5 with the updated and unalterable version provided at the end of L5

In the offer, the Applicant shall explain the approach to implementing the above MIP requirements.

Specify whether a MIP, QAP, ITS inspection and testing tttt

Pressure, and leak tests

As a minimum, the following tests shall be conducted during construction of the components.

- Pressure tests shall be performed in accordance with documentation in accordance with Pressure Equipment Directive (2014/68/EU).

- Leak tests:

  - Leak tests shall be performed at ambient temperature after the pressure tests.

  - All welds, that that will be at cold in the final system, shall be thermally shocked (e.g. by spraying liquid nitrogen on them) and then leak tested.

Electrical, wiring and control system tests

After mechanical assembly and cabling of any sub-assembly, the Contractor shall execute a complete electrical and wiring test.  The electrical and wiring tests shall include at least:

- Visual inspection of the cabling.

- Validate conformity with the electrical wiring diagrams.

- Validate correct labelling.

- Validate the grounding of all components and measuring of insulation resistance for all electrical wiring and electrical components.

- Validate correct functioning of all valves (including correct positioner setting).

- Validate the electrical cabinets (instrumentation, power supply and control) by injection of input signals and detection of output signals.

The QPLANT:CIS operation shall be tested in simulation mode before shipment.

Tests of components

Functional tests shall be performed at the manufacturer site to detect any faults before delivery and to confirm the performance.  At least, the following tests shall be performed:

- All helium compressors or pumps shall be tested individually.  At least the flow rate, pressures, temperatures, helium leak, noise level and vibrations shall be measured.

- Compressor motors shall be tested individually.  At least the power consumption, temperatures, noise level, vibrations and efficiency shall be measured

- Turbines, cold compressors, and cold circulators shall be tested at design rotation speed at ambient temperature.  At least vibrations, rotor stability and noise shall be measured.

- All cryogenic helium valves shall be delivered with leak test certificates of the body and the seat.

- All safety components shall be delivered with the necessary certificates.

Packaging, Transport and Storage

Prior to transportation, all process circuits of the QPLANT components shall be filled with inert gas at a fixed pressure and sealed during transport.  Pressure gauges shall be installed and checked at the departure from manufacturer premises and at the arrival on SCK CEN site.

Each package shall be clearly marked with a label stating the Contractor’s name, the destination, the name of the component and its identification number, the weight, and a link to the documentation.

Prior to transportation, the package units shall be visually inspected at the manufacturer premises and a certificate about proper packaging and availability of the necessary documentation shall be issued.  Representatives of the SCK CEN shall be invited by the Contractor to witness the inspection.

The Contractor is responsible for any intermediate storage and the transport of all the QPLANT components from the manufacturing sites to the final installation location including all loading, unloading and final positioning activities. The contractor shall document all packagaging and transportation in DD-7

Installation

The purpose of the (L4) Installation phase is to achieve Static readiness and integrity verification prior to cool-down, commissioning, and acceptance.

Incoming Inspection at SCK CEN Site

The Contractor shall perform at least the following actions:

- Inventory check

- Visual checks (damage, welds, packaging)

- Comparison of Pressure-retention readings before vs. after transport

- Read out Shock/acceleration indicators

- Submission of the Incoming Inspection Report

Installation & Pre-Commissioning prerequisites

Before initiation of Standalone Commissioning, the Contractor shall complete static verification activities to demonstrate that the system is ready for functional operation. These activities shall normally be completed by the Contractor prior to global plant startup.

During installation at SCK CEN site, the Contractor shall implement and submit a defined QA/QC governance structure that identifies who is responsible for installation quality, who approves installations for testing, and how deviations are escalated. This structure shall be consistent with the Responsibility Matrix and Project Board governance.

The Contractor shall establish and maintain an installation verification matrix linking the as-built installation to the approved design documentation, including P&IDs, 3D models, routing drawings and weld maps. The matrix shall define verification activities, acceptance criteria and responsible parties for confirming that the installed configuration conforms to the design before commissioning and provided as part of DD-8

Quality Assurance After Mechanical Assembly

The Contractor shall perform at least the following actions:

- Helium service line tightness verification

- Interface geometry verification

- Verification of conformance of assembly vs P&ID and 3D model

- Checking of Labelling and weld inspections

Static & Integrity Requirements

The Contractor shall demonstrate compliance with the following:

  - Pressure & Leak Integrity

- All pressure-containing components shall successfully pass pressure tests and static leak tests in accordance with the applicable codes. Pressure test shall be pneumatic on all helium service components (Note: Not applicable to process cooling (PS01) and heat recovery (HV06) items)

- Valid test certificates shall be provided.

  - Electrical & Instrumentation Verification

- Electrical continuity, insulation, and functional tests shall be completed.

- All instruments (including sensors, valves, and gas analysers) shall be calibrated and verified.

  - Safety Logic Verification

- All safety interlocks and fail-safe functions shall be checked to confirm correct behaviour under fault conditions.

  - Control System Verification

- Control procedures implemented in the process control system shall be verified for correct execution.

  - Cleanliness & Conditioning

- All gas circuits shall be conditioned and verified clean.

  - Initial/static vibration checks shall be performed on compressors.

  - Insulation Vacuum (Warm Condition)

- Prior to cool-down, the insulation vacuum of the cold box shall be verified to be below 10⁻³ mbar, unless a different value is justified based on operational history.

- Completion of L4 verification is a prerequisite for entry into Standalone Commissioning (L5).

Pre-Commissioning

The Contractor shall perform at least the following actions:

- Mechanical placement and alignment

- Interconnection to all site utilities

- Deployment of Temporary vacuum systems

- Compliance with site logistics + safety

- Submission of Installation Report DD-8

- Completion of L4 verification is a prerequisite for entry into Standalone Commissioning (L5)

Standalone Commissioning (L5)

Purpose: To establish stable automatic operation, tune control loops, and verify correct functional behaviour without manual intervention.

Prior to Standalone Commissioning, the Contractor shall submit a Standalone Commissioning QA/QC strategy describing test readiness reviews, commissioning risk assessment, test environments, safety measures, and the criteria for proceeding from Standalone Commissioning to integrated testing. The strategy shall reference the Project Quality Plan, MIP and the Codes and Standards Register.

The Contractor shall define and maintain a matrix of roles and responsibilities for commissioning and acceptance testing, identifying at least: Commissioning Manager, Test Leaders, SCK CEN Project Manager, QPLANT Technical Lead, QCELL representative, Contractor QA, and any third-party bodies. The matrix shall specify responsibilities for planning, executing, witnessing, approving, and documenting tests.

During Standalone commissioning, the Contractor shall commission the QPLANT without QCELL/QDIST integration. This includes e.g.:

- The PI parameters of the compressor pressure control loops shall be tuned to achieve stable suction and discharge pressures.

- Prepare the QPLANT for the SAT.

Tests to be done during Standalone Commissioning

The contractor shall perform at least the following tests:

- Pressure integrity

- Control & interlock logic

- Functional behavior of valves, heaters, turbines, compressors

- Warm/cold runs as feasible

- Instrument calibration + trending

- Validation of the correct functioning of the QPLANT:CIS

Functional Commissioning & Control Tuning

During Standalone Commissioning, the Contractor shall perform functional checks and tuning activities to demonstrate stable, automatic operation of the QPLANT. The following activities shall be performed:

  - Compressor Control Tuning

- PI control parameters for pressure regulation loops shall be tuned to achieve stable pressures without oscillation.

  - Vibration Spectral Analysis

- A vibration spectral analysis shall be performed during operation to identify potential vibration sources.

- The results shall serve as a reference baseline for the machine lifetime.

  - Adsorber Sequence Logic

- Automatic regeneration and switching sequences for warm and cold adsorbers shall be verified.

- Transitions shall occur without unacceptable temperature excursions.

  - Turbine Optimization

- Expansion turbines shall be optimized for rotational speed.

- Where applicable, labyrinth sealing parameters shall be tuned.

  - Pump-Down Simulation (< 4.5 K systems)

- A simulation of the pump-down and reconnection sequences shall be performed to verify control system behavior.

Performance and capacity Testing verification

Acceptance Testing shall validate compliance with all guaranteed performance, capacity, and quality criteria defined in this Technical Specification

A. Reliability & Quality Verification

The Contractor shall perform the following actions :

  - Long Duration Test

- The compression station shall operate continuously for a minimum of 24 hours at specified conditions to demonstrate thermal stability and mechanical reliability.

  - Cycle Gas Purity

- During long-duration operation, impurity levels (O₂, N₂, H₂O) shall remain equal to or lower than the guaranteed values.

  - Oil Removal Efficiency

- Bulk Separation: Oil concentration downstream of the bulk separator shall meet the specified limits.

- Coalescers: The efficiency of the first coalescer stage shall be verified after cartridge saturation.

  - Dryer Capacity

- The full-flow water retention capacity of the dryer shall be verified, potentially by controlled water injection.

Acceptance Testing

Purpose:
Final verification that the system meets or exceeds the contractual performance guarantees.

General Requirements

All proof tests, functional tests and control-system tests required by the applicable codes, standards and safety analyses shall be identified in the MIP and the Commissioning Plan, with clear test methods, acceptance criteria and responsibilities.  The Contractor shall demonstrate, by traceable documentation, that the executed tests fully cover the requirements of the relevant codes, standards, and safety studies, and that any periodic proof tests required during operation are clearly specified for handover to SCK CEN.

The test program shall be prepared and submitted by the Contractor to SCK CEN for review and approval at least 3 months prior to the date scheduled for the tests, unless otherwise specified.  The Acceptance Test(s) Program(s) shall describe:

  - General overview: the purpose of the tests, a comprehensive list of the tests to be performed, the participants to be present on site during the test, and a description of the communication strategy and logistical organization for conducting the tests.

  - General requirements: tools, instrumentation, and computing devices to be used; environmental conditions that must be in place; required consumables and utilities (e.g.: process gas, electricity, cooling water); qualifications of the personnel to conduct the testing.

  - Safety requirements which must be respected during the testing.

  - Parameters to be measured and their measurement accuracy, noting the target values, range of acceptability, on which test stage which parameters are measured, the measurement instruments used to perform the measurements, the measurement method, the calculation formulas (if no direct measurement is possible), ...

  - Test setups and methods, including a description of each test setup and the method used to establish an accurate measurement.

  - Reporting, including a description of how the acceptance tests shall be documented, what the documents shall contain and to what organizations these documents shall be transmitted.

  - The Acceptance Test(s) shall be documented in FAT/SAT reports, clearly documenting the results of each individual test and whether the deliverable has passed or failed the acceptance test (incl. applicable Non-Conformity reports).

The Contractor shall provide all equipment necessary to perform and to evaluate the FAT/SAT.  If needed, additional test cryostats, valves and instrumentation for acceptance tests shall be delivered by the Contractor.

Factory Acceptance Test (FAT)

Factory Acceptance Tests shall be executed under the control of the Contractor’s Quality Manager and Test Leader in accordance with the approved MIP and Commissioning Plan. All measuring and test equipment used for FAT shall be traceable to recognised calibration standards.  FAT results, deviations, corrective actions, and re-tests shall be documented in formal FAT reports submitted for SCK CEN review and approval.

The FAT program shall consider, as a minimum, the requirement outlined in §3.9.  SCK CEN and its representatives may witness these tests at the Contractor and his Subcontractor's sites.  SCK CEN shall approve the results before transportation.

Turbine Performance:
Performance testing of turbines is typically performed at the manufacturer’s facility (FAT). Site testing shall focus on verification against FAT reference data using available instrumentation.

Cryogenic Compressors:
Due to the absence of representative factory test loops, performance verification of cryogenic compressors shall be performed during site commissioning and acceptance

Site Acceptance Tests (SAT)

Site Acceptance Tests, including integrated tests with QCELL (to be proposed by Contractor at the end of L6 and handover documentation) and other interfaces, shall be performed according to an SAT programme agreed between the Contractor, SCK CEN Project Manager, QPLANT Technical Lead and User.  SAT results, punch lists, classification of punch items, and closure evidence shall be recorded and shall form part of the final acceptance and handover documentation

The SAT program shall consider, as a minimum, the requirements outlined in XXXX

SCK CEN and its representatives shall have access to participate to the tests on site.

The SAT report shall be included in DD-11 Acceptance Test File

The purpose of the SAT is to test the plant performance, functional demonstration.

The Contractor shall perform the SAT with SCK CEN witnessing.

During SAT, the User (or interface with QCELL/QDIST) cryogenic circuits (only simulated).

The contractor shall perform the following Capacity and Performance Demonstrations

- Compressor Performance – Nominal

  - For each compressor, the delivered mass flow shall be equal to or higher than guaranteed, and absorbed power equal to or lower than guaranteed during a 100-hour run.

- Compressor Turn-Down Performance

  - Performance measurements shall be repeated at reduced mass flow rates and suction pressures as specified.

- Thermal Shield Power

  - The system shall demonstrate absorption of the design thermal-shield power while maintaining discharge temperatures at or below design values.

- Liquefaction Capacity

  - The liquid helium production rate shall be measured and shall meet or exceed the guaranteed value.

- Mixed-Duty Operation (if applicable)

  - Simultaneous refrigeration and liquefaction performance shall be demonstrated.

  - Supercritical helium temperature shall remain equal to or lower than guaranteed.

- Sub-4.5 K Performance (Cryogenic Compressors)

  - Available refrigeration power and suction-pressure stability shall be verified against design specifications.

- Storage Heat Leak Verification

  - Boil-off rates for liquid helium and/or nitrogen storage shall be measured and shall not exceed guaranteed heat-leak values.

SAT General

The following entry conditions shall apply before commencing with the SAT:

- Standalone commissioning fully complete

- All interface control logic between QPLANT:CIS and: MCS, MIT and MIS activated

- Required helium inventory is on site

- Safety systems validated – this means safety system in already during commisoign – we ask again for demonstration of some and proof of all

- Exit condition: Approval to start subsystem SAT tests

WCS Testing

The Contractor shall perform the following tests for the WCS:

- VLP/LP (LPC) and LP/HP (HPC) compressor functionality

- Recovery and inventory management and warm panel integtegrated scenario testing (LOOP, LOIA, recovery via S-line (flow from QRB and flow from QCELL) – demonstrate handling of this step change (in flow), purity of the gas, any conditioning of line (permanent flow from QVE side? Minimum flow to avoid stagnand and detoriation

- Oil-removal efficiency

- Dryer performance

- Noise, vibration, flow stability

- Load/unload logic, turndown control

- Helium Recovery and Inventory management system

- WCS Warm Panel gas routing functional demonstration

- Cooling turndown and balance of load between HV06 and PS01

  - LOCA for PS01, LOCA for HV06 (see Interfaces)

- Exit criteria: Verified stable operation across all pressure levels

QPLANT Functional Tests

The Contractor shall perform the following Tests:

- Full control-sequence validation of QRB + WCS

- Turbine performance, cold-compressor regulated operation

- Adsorber switching/regeneration

- Instrumentation accuracy cross-checks

- Alarms, protections, interlocks

- Exit criteria: Verified automatic & safe transitions in controlled conditions

- Next state: SAT-QPLANT-CAPACITY

QPLANT Capacity Tests

The Contractor shall perform the following Tests:

- Achieve and sustain required refrigeration power

- Validate invCOP and mass-flow capabilities

- Demonstrate performance at nominal & reduced loads

- Error calculations for all performance measurements

- Exit criteria: Capacity ≥ Requirements  (Nominal & Minimal Design Points) – See Table 3

- Next state: SAT-TS-STANDBY

Steady-state Test

Thermal Shield Standby

The Contractor shall perform the following Tests:

- Bring TS circuit to 40/60 K

- Verify flow, ΔT stability, pressure drop, regulation loops

- Exit: Temperature + control stability demonstrated

- Next state: SAT-COLD-STANDBY

4.5 K Standby

The Contractor shall perform the following Tests/Tasks:

- Transition QCELL + distribution to ~4.5 K

- Confirm stable SHe supply/return behaviour

- Validate cold-box load balancing

- Exit: Stable 4.5 K standby state

- Next state: SAT-2K-BASELINE

2 K Operation/2K Steady state

The Contractor shall perform the following Tests

- Establish 2 K (27 mbar) conditions (GIVE more details – Coldcompressor startup and dependencies. Start of PVPS and CC and response to step change or scenario, config or heat load change.
DEMONSTRAT the pressure stability – see RTM-XXXX

- Demonstrate cold compressor operating window and stability window
(give the image as input from DBE – total allowed change, vs variance, vs long term – speed of change) to remain stable – this done via 10 USER defined ‘Operational Points’ – within the TOTAL design envelope (2K_ SB, 2K_SB, 2K_OP, 4K SB, TS_SB also random transisions between points (see ANNEX for details 10 random operation points – MIN to MAX
MIN to MAX 24, 30
Updated heat load tables

- Validate coupler cooling return (QRB.W) as constant and participatory flow returning at 300 K with the specific impact simulated and WITNESSED

- Verify thermal-stability margins (for RF operation readiness)

- Exit: Sustained 2 K conditions with all performance metrics demonstrated and stable

- ABNORMEL and STRESS test – choke and surge confirmation – isentropic efficiency measurement, update of TestS (Test System) and modeling input

QPLANT Transition Tests

The contractor shall validate all operational scenario transitions from Fig. 6.  Transitions include:

- Warm Stop ↔ TS Stand-by

- TS Stand-by ↔ 4.5 K Stand-by

- Liquid Filling, Inventory removal – isothermal generation or consumption of QCELL internal LHE

- 4.5 K Stand-by ↔ 2 K Stand-by

- 2 K Stand-by ↔ 2 K Operation

- 2 K Operation → emergency transitions (LOOP, trips, adsorber regen)

- Cool-down sequences (parallel/TS-first)

- Warm-up sequences (passive, heater-assisted)

- Derogated 8 K supply (from nominal 4.5 K) at the QRB.A supply side to suppress any 2 phase flow during User progressive installation that involved ADB testing without connected QM (or as an optional) operational state – This similar to 4.5 K stanby (higher supply temperature)

- Exit criteria: All state transitions meet rate limits, stability criteria, and automatic execution requirements, with SCADA and data_historian reproducing the full test and temporal data for ‘off-line’ viewing and validation

SHOW the ‘lack of operator input needed during full 300 to 4.5 and the liquid filliing and the 4.5 to 2K with QCC

- Final state: SAT-PASSED → Eligible for FINAL ACCEPTANCE under §8.4.

Spare Parts

- In the offer, they need to give us the list of strategic spare parts needed for 5/10 years.  And a price for the whole package.  This is the contingent part

The Contractor shall ensure that all spare parts delivered under the Contract are traceable to qualified manufacturers and are compatible with the original design and performance requirements.  For critical spare parts relevant to reliability and availability, the Contractor shall provide certificates of conformity, recommended stocking levels and any specific quality requirements needed to support reliability-centred maintenance over the lifecycle.

During Contract execution, the Contractor shall expand this list into a detailed breakdown, including part references, failure assumptions, and cost drivers.  A corresponding spares inventory shall be defined, including shelf life and storage constraints, in alignment with the Reliability-Centered Maintenance (RCM) Plan.

The Contractor shall maintain and provide an up-to-date internal inventory of all components, equipment, and services delivered as part of the plant.  This inventory must include detailed information on internal applications, devices, network interfaces, and communication protocols used within the plant.  The internal inventory should be updated and shared with the client whenever any changes or updates occur in the plant.

In their Offer, the Applicant shall provide a detailed list of all recommended maintenance and capital spare parts required to support the first five (5) years of operation.  This list shall include:

- Identification and description of each spare part.

- Preventive maintenance and repair recommendations.

- Unit price plus price revision formula

- Delivery lead times and any associated storage or handling requirements.

- The Applicant shall pay particular attention to operationally critical components—such as turbines, cold compressors, and warm compressors—with long procurement lead times.  These shall be exhaustively identified and justified within the spare parts strategy.

In its Offer, the Applicant shall provide a top-level list of all Components that meet either of the following criteria:

- a mean time between failures (MTBF) of less than ten (10) years, or

- a projected replacement rate of two (2) or more times within a forty (40)-year service life.

- This list shall focus on cost-relevant or operationally critical items and need not include minor components where individual replacement costs or impacts are negligible.

After-sales Services

Level Agreement (Option 3)

It provides one (1) year of post-commissioning operational support.  SCK CEN may, by mutual agreement, extend the SLA for one (1) additional year.  The SLA expressly excludes integrated commissioning activities that involve end-user participation (e.g. Control and Interlock System (CIS) interfacing or operational testing performed by SCK CEN personnel).  Such activities fall outside the Contractor’s contractual obligations.  For scope details and exclusions, refer to Section 2.1.

Lifetime After-sales Services (applicable when Option 3 is exercised)

If SCK CEN activates Option 3 at contract award, the Contractor shall provide after-sales services for the full lifetime of the QPLANT.  These services shall include, as a minimum:

- A helpdesk offering remote technical support on Business Days from 07:00 to 19:00 CE(S)T, accessible by telephone, Microsoft Teams, or equivalent tools.  The Contractor shall acknowledge each defect notification within twenty-four (24) hours.

- Technical field service to intervene on-site for unforeseen issues requiring corrective maintenance.

- An annual maintenance programme covering predictive and preventive activities across all QPLANT subsystems.

- Comprehensive fault identification, analysis, troubleshooting, and general technical assistance for electrical, mechanical, controls, software, and firmware matters.

- Deployment only of personnel suitably qualified and experienced for the relevant QPLANT systems.

Upon receipt of a support request from SCK CEN, the Contractor shall:

- Complete fault identification and establish a remediation strategy, including preliminary cost and time estimates (step (i)):

  - within three (3) Business Days when on-site presence is unnecessary

  - within five (5) Business Days when on-site presence is required.

- Propose a remediation plan that minimises LINAC downtime.

- Submit a firm quotation for the solution within three (3) Business Days after completing step (i).  The quotation shall state:

- a technical description of the proposed solution

- fixed price for implementation.

- lead time for execution.

- Provide the solution without undue delay once SCK CEN issues a purchase order or written approval.

The Contractor’s offer shall include:

- A concise description of the after-sales service organisation, including escalation paths and staffing overview.

- Clear procedures for requesting support, listing all contact channels and their availability.

- Pricing of after-sales services, including labour hourly rates.  Spare parts or components required for after-sales activities shall be remunerated at prices not exceeding those listed under § 3.8.1.11 “Spare Parts Supply.”

Documentation and Deliverables (DD-#)

Requirements concerning specific deliverables or documents, These documents shall be included in the Deliverables List (DD-#) and submitted in editable electronic format and, where requested, in hard copy.

The Contractor shall provide all quality-related documentation identified in the Project Quality Plan, including but not limited to: Project Quality Plan, Manufacturing and Inspection Plan / Inspection and Test Plan, Responsibility Matrix, Change Register, Non-Conformity Register, audit reports, FAT reports, SAT reports, commissioning reports and installation dossiers.

The Contractor shall organise the applicable codes and standards in a hierarchy where management-system standards (e.g. ISO 9001) act as parents to project-level requirements, and technical standards (e.g. PED, EN 13480, EN 13445, IEC functional-safety standards) define detailed design, manufacturing and test requirements. For each requirement in Chapters 3 and 4, the Contractor shall demonstrate traceability to one or more entries in the Codes and Standards Register.This shall be submitted with the updated QAP after project kick-off meeting

All project-related documents, including but not limited to the CAD model, shall be uploaded to the SCK Coreshare platform.

All documents shall follow standardized file naming conventions and metadata formats to ensure clear identification, version control, and lifecycle management.

Throughout Contract performance the Contractor shall, at a minimum, deliver the documentation listed in Table 17.

As part of #DD04, the Contractor shall provide the necessary technical data and design datasheets of critical components such as heat exchangers, piping, rotating machines, and valve information with sufficient detail to allow SCK CEN to model the complete cryogenic system including the cryogenic plant in simulations.

The Contractor shall deliver a maintenance manual and lifecycle strategy documentation, including but not limited to:

- Spare inventory and obsolescence plans

- PPE, alarms, and recovery training

- Simulation-driven scenario testing

- OPEX estimations.

- Maintenance checks, functional testing

- MTBF-based planning and condition diagnostics

- Operator commissioning and technician maintenance and replacement involvement

- Real-time MTBF vs prediction curve tracking

The process flow diagrams, process and instrumentation diagrams and temperature-entropy diagrams showing all the operation modes (including cool down) of the QPLANT shall be subject to approval by SCK CEN.

The Contractor shall, at the Preliminary Design Review (PDR), which is the end of the L1 (Concept Design), provide 3-D CAD cut-aways and maintenance envelopes demonstrating safe human access to all QRB components and instrumentation located inside the vacuum vessel.

The Contractor should use EPLAN for all electrical and masterplan-related drawings to facilitate integration of the deliverables into SCK CEN’s existing design and facility documentation systems.  While this is not mandatory, SCK CEN encourages its use to enhance compatibility with internal tools and infrastructure.

The Contractor should ensure that the 3D models and associated workflows are compatible with SCK CEN’s current digital engineering environment, which includes PTC Windchill, PTC Creo, and Autodesk BIM360.

In the offer the Applicant shall:

- describe the Contractors digital engineering environment

- propose a suitable workflow for 3D model exchange,

- describe how the Contractor intends to use model metadata and attributes, and

- explain how the Contractor will ensure integration and interoperability with SCK CEN’s systems throughout the project lifecycle.

Table 17 Documentation and Deliverables

| Deliverable ID | Title / Content | Phase | Due Date / Milestone |
| --- | --- | --- | --- |
|  | Project Management Plan (execution of project) including management dashboard, schedule, meeting processes, doc list, reporting/storage | Project Management (L0, L1) | SIG + 1 month |
|  | Quality Assurance Plan, including compliancy matrix, test plans (incl. control system), reports, functional safety lifecycle, certificates mgmt., NCR/CR processes | QA/QC (L1) | SIG + 1 month |
|  | Conceptual Design File: description of Cryoplant, PFDs/P&IDs, T–s diagrams, process calcs, plant layout & CAD models, utility requirements | Conceptual Design (L1) | SIG + 5 months |
|  | Detailed Design File: final P&IDs, T–s diagrams, calculation notes, list of components, interface list, detailed drawings, safety report, control system architecture, procurement specs, spares list | Detailed Design (L2) | SIG + 9 months |
|  | Manufacturing & Inspection Plan (MIP): test program, FAT, commissioning & acceptance tests, fabrication & welding reports, certificates, instrumentation/electrical documentation | Construction (L3) | SIG + 12 months |
|  | Cryoplant Control System Dossier: draft & final programs, source code (Bitbucket), alarms/signals list, architecture, software documentation, calibration certs | Controls (L1, L2, | DD05 + updates |
|  | Packaging & Transportation Plan | Manufacturing (L3) | Before shipment |
|  | Installation File: incoming inspection, installation tests, assembly reports, certificates, Non-Conformity handling | Installation Phase (L4 | Prior to commissioning |
|  | Commissioning File: commissioning procedures, test reports, operator involvement, maintenance training, functional tests, SAT | Commissioning | End of commissioning |
|  | Acceptance Test File: FAT & SAT reports, performance verification, acceptance protocols | Acceptance | End of Acceptance Tests |
|  | Final Documentation File: operation manual, maintenance plan, spare parts plan, lifecycle strategy, final reports, complete doc package | Acceptance testing | 1 month after Acceptance |
|  | Reliability-Centred Maintenance (RCM) & Lifecycle Cost Management (LCM) Plans: MTBF data, spares, OPEX, preventive functional test plan | Lifecycle Mgmt. | With DD12 |
|  | CAD Models & 3D integration files (Creo/STEP/BIM), uploaded to SCK Coreshare with metadata | Throughout | At each design milestone |
|  | OEM Documentation: datasheets, manuals, certificates (COTS equipment) | OEM phase | Along supply |
|  | - VLAREM dossier: Noise Study | Detailed Design |  |

OEM Documentation

Documentation from OEMs (COTS Equipment)

The Contractor shall store and provide to SCK CEN all documentation received from the Original Equipment Manufacturer (OEM) related to Commercial Off-The-Shelf (COTS) equipment and applicable use within the QPLANT

OEM Documentation Provided by SCK CEN

If SCK CEN provides OEM documentation to the Contractor, the Contractor shall store and return the documentation to SCK CEN as received.  If the original documentation is in a language other than English, the Contractor shall provide an accurate English translation alongside the original.

The Contractor shall version-control the documents received from SCK CEN.  When an updated version of a document is received, the previous version shall be removed from circulation as soon as reasonably possible.

These documents shall be made accessible to the Contractor’s employees / Subcontractors only on a need-to-know basis, for the purpose of the Contract, for a limited time, for as long as the documents are needed.

Safety, Codes and Standards

For pressure equipment and associated piping, the Contractor shall assume the role of Manufacturer (or equivalent designation under the applicable pressure equipment legislation and standards) and shall be responsible for design, manufacturing, conformity assessment, marking and documentation in accordance with Pressure Equipment Directive (2014/68/EU). These responsibilities shall be clearly reflected in the Responsibility Matrix and the Codes and Standards Register which form part of continuously updated QAP DD-2

The Contractor shall demonstrate how its existing ISO 9001:2015 Quality Management System is applied to the QPLANT project, with explicit reference to the clauses relevant to this scope, including at least: 5.3 (roles and responsibilities), 8.3 (design and development), 8.4 (control of external providers), 8.5 (production and service provision), 8.6 (release of products and services) and 8.7 (control of nonconforming outputs). The Contractor shall provide project-specific procedures or mappings rather than generic manuals where necessary for effective follow-up by SCK CEN.

The Contractor shall organise the applicable codes and standards in a hierarchy where management-system standards (e.g. ISO 9001) act as parents to project-level requirements and technical standards (e.g. PED, EN 13480, EN 13445, IEC functional-safety standards).

Safety

Burst disk outlets shall be routed to avoid cold burn or asphyxiation risks.

Emergency or rapid venting operations shall be executed via the S-line (QINFRA.S) or by direct QCELL bursting disk exhaust (not part of QPLANT scope) venting to atmosphere as designed.  Transfers of inventory to QINFRA shall be performed only in accordance with approved safety procedures, after verification that no personnel are present in affected areas, and with active monitoring and relief provisions in place.

For any 3rd party (e.g. PED auditor) inspection or certification needed for requirements compliance, the Contractor shall bare the full cost and should preferentially use the SCK CEN nominated local representative unless logistically not possible.

The Contractor shall propose oxygen‑deficiency‑monitor (ODH) locations; final placement approved by SCK CEN.  The Contractor shall recommend and guide SCK CEN to define the location of the oxygen deficiency detectors in the QPLANT buildings.

NOTE: SCK CEN is responsible for ODH sensors and linking to site alarm and access control.

Redundant measurement channels and stand-by heaters shall be provided for all inaccessible components and for components whose failure would jeopardise operation or safety.

Cold helium volumes shall be protected by safety devices in accordance with EN 17527 (supplemented, where applicable, by API 520/521/580 for warm service).  Any cold volume that can be isolated by valves, plus all insulation vacuum volumes, shall have dedicated safety devices.

Safety exhausts shall be collected  where feasible or safely vented to the outside.

Hazard definitions and typical mitigation devices

| Hazard category | Terminology | Typical detection / protection device | Notes (cryogenic helium context) |
| --- | --- | --- | --- |
| Reduction of ambient O₂ below safe physiological limits | Oxygen-Deficiency-Hazard (ODH) | Fixed ODH monitor (electro-chemical or paramagnetic cell) | Primary life-safety hazard during helium releases or continuous Safety-Line venting. |
| Complete deprivation of oxygen to the body | Asphyxiation / anoxia | — (medical condition; not detected by plant instrumentation) | Final consequence if ODH is not mitigated. |
| Local freezing of tissue due to contact with cryogens | Cold burn (cryogenic frostbite) | IR skin sensor, PPE requirement, duty-holder training | Secondary hazard during liquid discharge or cold-gas impingement. |

ODH Monitoring Architecture and Responsibilities

Free-Issue Equipment (FIE)

Fixed ODH monitors, compliant with EN 50104:2019 and rated to performance class SIL-2, shall be supplied by SCK CEN. SCK CEN retains responsibility for the certification and demonstration of SIL-2 compliance for the instrumentation forming part of the ODH safety function. – THE QPLANT shall demonstrate the integration with this system – functional and interlocks and triggers.

Contractor Responsibilities

The contractor shall:

- Install, cable, configure, and commission all ODH monitors provided by SCK CEN.

- Ensure the electrical signal from each sensor is split and redundantly routed:

  - One signal path to SCK CEN systems (for SIL validation), and

  - One signal path to QPLANT:CIS (for local alarms and interlocks).

- Integrate all alarm thresholds, zoning logic, and mitigation responses into QPLANT:CIS.

- Perform functional testing of all ODH alarm chains during QPLANT acceptance.

- Identify the optimal number and location of sensors required to cover the compressor room and coldbox room, based on helium Worst-Credible Scenario (WCS) leak analysis.

Interface Clarification

SCK CEN retains full functional authority over all ODH safety signal paths.  Integration of these signals into QPLANT:CIS must not interfere with or compromise the SIL-2 certified safety loop.  The signal duplication is for plant alarm and interlock logic only.

The Contractor shall install, cable, configure, and commission the Free-Issue Equipment (ODH monitors), integrating them into the QPLANT control and safety systems.

The Contractor shall ensure the electrical signal from each sensor is split and redundantly routed:

- One signal path to SCK CEN systems (for SIL validation), and

- One signal path to QPLANT:CIS (for alarm integration and interlocks).

The Contractor shall implement the physical and logical integration of ODH signals into QPLANT:CIS, including alarm thresholds, zoning logic, and mitigation responses.  Functional verification and end-to-end testing of all ODH alarm functions shall be demonstrated during QPLANT acceptance.

The Contractor shall install the owner-supplied ODH monitors at every access point and in each enclosed zone where a credible helium release could reduce ambient O₂ below 19.5 % (v/v) within 60 seconds under WCS leak conditions.  Sensor positioning, cabling, and functional tests fall under Contractor scope.

The Contractor shall provide all technical inputs required for SCK CEN to complete the final ODH configuration and SIL justification.  At minimum, this includes:

- Helium inventory (by zone),

- Piping layout drawings and enclosure volumes,

- Leak rate assumptions based on QPLANT operational scenarios,

- Ventilation performance data,

- Defined ODH zoning boundaries and access control criteria.

In the offer the Applicant shall explicitly state explicitly whether the ODH system status (e.g. alarm thresholds reached, zone evacuation triggered) constitutes a functional input to QPLANT:CIS logic.  If applicable, the Offer shall describe the intended system behaviour, logic dependencies, and impact on cryogenic system operation (e.g., automatic warm-up, valve interlocks, or shutdowns).

SCK CEN shall retain overall responsibility for the ODH system's compliance with functional safety requirements.  The signals from all ODH sensors remain under SCK CEN ownership, and their duplication to QPLANT:CIS shall not alter or interrupt their role in the certified safety chain.

Control Systems and PLC safety

Internal interlocks: The QPLANT shall not rely on the MIS, unless the interlock must be propagated to or relies on other systems.

Interlock status to MCS: The QPLANT shall ensure that the status of each interlock is monitorable through the MCS control interface.

Personnel protection standards: When the system has personnel protection, the systems personnel protection shall be designed according to standards IEC 61508 (Functional Safety) or one of the sector-specific derived standards (IEC 62061, IEC 61511) or alternative (e.g. ISO 13849-1).

Hard-Wired Safety-Interlock Instrumentation

The Contractor shall design and implement fail-safe, hard-wired interlock circuits (i.e. dedicated relay or safety-PLC loops that remain fully functional in the event of a control-system failure) to prevent mechanical or thermal damage to the following critical equipment classes: compressors, turbines, pumps, and electrical heaters.

Electrical contacts associated with the hard-wired interlock sensors (flow, pressure, temperature, level, valve-end switches, etc.) shall be wired “positive-logic” (open = abnormal/trip) so that any loss of signal, power, or cable integrity forces the affected component to a safe state.

The Contractor’s own risk assessment shall determine the final list of equipment, set points, and reaction times

- the resulting safety-interlock list hall be submitted with the Detailed Design file.

- Safety-significant or reliability-critical SSCs such as sensors and instrumentation, control and shut-off valves, pressure relief devices and bursting disks, actuators, regulators, and any components affecting operational safety or availability.

Codes and Standards

The Contractor shall provide an EU declaration of conformity for the QPLANT and CE mark all QPLANT components.  Therefore, the Contractor shall at least:

- Identify all EU directives applicable to the QPLANT and ensure compliance with said EU directives.  The directives listed below are identified by SCK CEN as a minimum requirement but does not exclude other directives from being applicable:

- Low Voltage Directive 2014/35/EU

- Machinery Directive 2006/42/EC

- EMC Directive 2014/30/EU

- Pressure Equipment Directive (2014/68/EU)

The contractor shall identify the applicable standards (harmonized or non-harmonized), and technical specifications that support compliance with the essential requirements outlined in the EU directive(s).

- The Contractor shall Submit the technical file, at the latest before shipment to SCK CEN of QPLANT parts, to demonstrate conformity with the directive(s).  The technical file shall include:

- A general description of the QPLANT

- An overall drawing of the product, as well as other drawings to cover specific aspects of the product, such as circuit diagrams.  The drawings shall, where appropriate, be accompanied with descriptions and explanations to understand the product.

- The HAZOP reports for QPLANT

- The Interfaces with other SCK CEN systems:

  - The description of the protective measures implemented to eliminate identified hazards or to reduce risks and, when appropriate, the indication of the residual risks associated with the QPLANT.

  - The list of standards and other technical specifications used to show compliance with the essential requirements outlined in the EU directive(s).

  - Instructions and other information for the safe use of the product covering at least, but not limited to, handling, shipping, installation, integration, operation, maintenance, de-commissioning, disposal, ... in English, and Dutch

  - Where appropriate, copies of the EU declaration of conformity of components incorporated into the assembly.

  - A copy of the QPLANT EU declaration of conformity in the original language, in English, and Dutch.

  - A copy of the nameplate(s) with CE mark.

- The Contractor shall submit specific detailed parts of the technical file, when requested by SCK CEN, to demonstrate conformity with the directive(s) in English.  The detailed parts of the technical file are:

  - Full detailed drawings.

  - Calculation notes,

  - Test reports, certificates, ...

Electromagnetic interference

The Contractor shall propose a solution, subject to approval by SCK CEN, to minimize the effects of electromagnetic interference (EMI) as referenced in [AD 7].  The solution shall address shielding, cabling, signal routing, voltage level separation, and grounding strategy.

The EMI mitigation design shall ensure that all instrumentation and control signals operate within their specified accuracy limits under defined electromagnetic environments.

The proposed solution shall comply with the relevant sections of EN 61000-6-2 (Immunity for industrial environments) and EN 61000-6-4 (Emission for industrial environments), or an equivalent standard approved by SCK CEN.

- Verification shall be performed by means of:

- A design review dossier including EMI layout drawings and shielding measures,

- A wiring and installation checklist verified during site inspection,

- And, where applicable, EMC type tests or certificates for sensitive components (e.g., sensors, analysers, PLCs).

To ease diagnostic and checking of measurement chains, knife-switch type terminal blocks or similar cabling interface shall be fitted for input and output signals connections with the QPLANT:CIS.

Pressure Equipment & Safety

Table 18 Pressure Equipment and Safety Standards

| Ref | Standard | Scope |
| --- | --- | --- |
| PED | 2014/68/EU | EU Pressure Equipment Directive |
| ASME VIII‐1 | Unfired pressure vessels | Design / certification |
| EN 13445 | Unfired pressure vessels | EU compliance |
| API 520/521 | Pressure relief sizing & selection | PSVs / BD |
| EN ISO 4126 | Safety valves & RD devices | Proof-test ≤ 5 y |
| ISO 21013-1/2 | Cryogenic safety devices | LP & HP vessels |

Functional Safety & Control

Table 19 Functional Safety & Control Standards

| Ref | Standard | Scope |
| --- | --- | --- |
| IEC 61508 | Functional safety (E/E/PE systems) | SIL assignment |
| IEC 61511 | SIS for process industry | SIS lifecycle |
| IEC 60204-1 / 61439 | Electrical equipment & switchgear | Control cabinet |
| IEC 60300-3-3 | RCM assessment | Links to DMAIC Control |

Asset & Maintenance Management

Table 20 Asset & Maintenance Management

| Ref | Standard | Scope |
| --- | --- | --- |
| ISO 55000 | Asset management lifecycle | 40-y RCM plan |
| ISO 14224 | Reliability & maintenance data | MTBF reporting |
| IEC 60300-3-12 | Life-cycle costing | CAPEX/OPEX modelling |

Cleanliness & Purity

Table 21 Cleanliness And Purity

| Ref | Standard | Scope |
| --- | --- | --- |
| ISO 8573-1 Class 0 | Oil-free compressor classification | Compressors |
| ASTM D5464 | Helium purity test | Getter skid validation |

Proof-Test & Control-Phase Requirements

Proof-test intervals: PSVs/BDs ≤ 5 years; SIL sensors ≤ 3 years; logic proof ≤ 4 years.

RCM linkage: Tests scheduled in RCM manual per ISO 55000 / ISO 14224.

The Contractor shall provide to SCK CEN the applied codes, rules and standard for the design, manufacturing, and testing of the QPLANT.

Schedule

Contractual performance shall proceed in phases (5.1).  These phases represent the highest-level breakdown of work packages expected for the project.  A phase will be considered as completed when all associated deliverables (Table 17) are approved by SCK CEN.  In their offer, the Applicant shall develop the phases according to its own expertise and experience and propose a detailed work schedule.  In doing so, the Applicant shall take into consideration the preliminary schedule in 5.2 by including the milestones and respecting the milestone dates provided in Table 23. The Applicant may add (to a reasonable extent) additional milestones as they think appropriate.

Table 22 Project Lifecycle Phases.

The active project runs from T0 at start of L1 to L6.

Contractual Phases

Design and Development (L1 Conceptual Design and L2 Detailed Design)

Activities expected to be performed in during the L1-Conceptual Design and L2-Detailed Design this phase shall, at least, include:

- Establishing the project management baseline (Management Dashboard & underlying processes, Quality Assurance Program and Risk Management Plan) for review and approval by SCK CEN.

- Developing the conceptual design, verifying/ validating conformance with technical specifications, defining specific requirements for buildings and utilities and preparing/ submitting the Conceptual Design File for review and approval by SCK CEN.

- Developing the detailed design, verifying/ validating conformance with technical specifications, defining the list of components (incl. procurement specifications, manufacturing drawings), setting final requirements for buildings and utilities, developing plans and procedures for the next phases (e.g. MIP, packaging and transportation plan, installation plan) and preparing/ submitting the Detailed Design File

Procurement, Assembly and Manufacturing (L3)

- Activities expected to be performed in this phase shall, at least, include:

- Procurement/ manufacturing of components and services necessary for performing the Contract, execution/ reporting of tests and inspections (incl. FAT), Non-Conformity handling, preparing final plans and procedures for Phase III and IV and preparing/ submitting the Procurement and Manufacturing File for review and approval by SCK CEN.

Installation (L4)

Activities expected to be performed in this phase shall, at least, include:

- Transportation to SCK CEN (only after manufacturing QC and FAT shall be approved by SCK  CEN), incoming inspections of supplies, installation of QPLANT, execution/ reporting of assembly tests, Non-Conformity handling and preparing/submitting the Installation File for review and approval by SCK CEN.

Phase I – Commissioning and Acceptance (L5-L6)

Commissioning and Acceptance testing may not necessarily follow a strict sequential order (as a part of the system may require successful acceptance to initiate commissioning and vice versa).  The Contractor shall develop the phase according to its own expertise and shall at least include the following activities:

- Stand-alone commissioning of the QPLANT, integrated commissioning with controls, non-conformity handling and preparing/ submitting the Commissioning File  for review and approval by SCK CEN.

- Execution/ reporting of SAT and preparing/ submitting the Acceptance Test File (for review and approval by SCK CEN.

- Project closure and submission of the Final Report for review and approval by SCK CEN.

Preliminary Schedule

Table 23 Preliminary Schedule and Main Milestones

“ED” = Earliest Date, “LD” = Latest Possible Date, “M” = months, “wks” = weeks, “BD” = Business Days, “CD” = Calendar Days.

| ID | Description | Responsible | Dates |
| --- | --- | --- | --- |
| TO | Contract Conclusion | SCK CEN | ED: Q2 2026 |
| Phase I -Design and Development |  |  |  |
| M11 | Kick-Off meeting | SCK CEN | T0 +15 BD |
| M12 | Management Dashboard & QAP submitted for review/approval | Contractor |  |
| M13 | Risk Assessment/ Management Plan submitted for review/approval | Contractor |  |
| M14 | Preliminary Information on Site Infrastructure delivered | SCK CEN | M11 + 1M |
| M15 | Deliverables associated with M12 and M13 approved | SCK CEN |  |
| M16 | Conceptual Design File submitted for review/approval | Contractor |  |
| M17 | Detailed Design File submitted for review/approval | Contractor |  |
| M18 | Detailed Design File approved | Contractor |  |
| Phase II – Procurement and Manufacturing |  |  |  |
| M21 | Manufacturing started | Contractor |  |
| M22 | Installation Plan submitted for review/approval | Contractor |  |
| M23 | Manufacturing completed | Contractor |  |
| M24 | FAT approved | SCK CEN |  |
| Phase III – Installation |  |  |  |
| MXX Building ready for installation |  | SCK CEN | XXXX |
| Infrastructure provided by SCK CEN ready |  | SCK CEN | XXXX |
| M31 | Incoming Inspection Report submitted for review/approval | Contractor |  |
| M32 | Installation started | Contractor |  |
| M33 | Installation completed | Contractor |  |
| M34 | Installation & Assembly Test Report submitted for review/approval | Contractor |  |
| Phase IV – Commissioning and Acceptance |  |  |  |
| M41 | Commissioning Test Report submitted for review/approval | Contractor |  |
| M42 | Acceptance Capacity testing started | Contractor |  |
| M43 | SAT Report submitted for review/approval | Contractor |  |
| M44 | Provisional Acceptance and handover | SCK CEN | T0 + 34 M |

Hold and Witness Points

Throughout the performance of the Contract, at least the following review/inspection (by SCK CEN) steps shall be implemented:

  - Hold Points

- FAT approval in view of shipments

- Approval Incoming Inspection Report in view of start installation

- Approval Installation and Assembly Test Report in view of start commissioning

- Approval Commissioning Test Report in view of start acceptance capacity testing

  - Witness points

- Approval of the Conceptual Design File

- Approval of the Detailed design File

- Approval of the Procurement and Manufacturing File

- Approval of the Installation File

- Approval of the Commissioning File

- Approval of the Acceptance Test File

- Approval of the Final Report

Upon receiving the Contractor’s finalized project schedule and Manufacturing and Inspection Plan, SCK CEN reserves the right to add or remove HP(s)/WP(s) from those currently foreseen and will duly notify the Contractor of such decisions.

SCK CEN has at its disposal a maximum of 30 Calendar Days (60 Calendar Days when involving (an) external partner(s)) to complete all formalities) concerning approval of a certain Hold Points.  Nonetheless, SCK CEN shall always aim to give feedback to the Contractor concerning the HPs without undue delay.  The envisaged lead time is 10 Business Days (to be determined considering SCK CEN’s and/or its collaboration partner’s days of closure)

Contract Performance

General Organization

In accordance with article 20.1 of Addendum I, the Contractor shall assign a member of its staff to be responsible for the follow-up of the Contract (further referred to as “Project Manager”).  The Project Manager shall be responsible for planning, organizing, monitoring, and controlling, and directing the performance of the Contract, to ensure that the Contract is accomplished on time, within budget, and compliant to the requirements laid down in the Contract.

The Contractor shall notify SCK CEN in writing in case a different Project Manager is appointed.  Replacement of the Project Manager is subject to prior written approval by SCK CEN.  In case of replacement, the substitute shall always have a level of education, skills, and experience equivalent to or better than the original resource proposed for this role.

At the conclusion of the Contract, SCK CEN shall designate the Leading Officer for the Contract and inform the Contractor.  The Contractor shall be notified of any change in writing.

Regarding the practical follow-up of the Contract, SCK CEN reserves the right to have itself represented by a third party of its choice, acting on its behalf (further referred to as “Representative(s)”).

In this respect, SCK CEN grants to the Representative(s) the same rights as SCK CEN have accrued under the present Contract and the Contractor shall give effect thereto.  The Contractor shall grant the Representatives the same access rights (physical access, document access, ...) as have been contractually instated for SCK CEN.

Notwithstanding the foregoing, SCK CEN will remain the sole principal to the Contract and therefore:

- any approval/acceptance/equivalent step which has been contractually set, shall only be approved, respectively accepted, if and to the extent that SCK CEN has confirmed its approval, respectively acceptance, of such step in writing.

- any decision to deviate from the terms and conditions as have been contractually agreed upon, may only be implemented after having obtained approval thereto from SCK CEN in writing.

Communication

All communication, including - but not limited to - tender documents, offers, technical documentation, any correspondence, and all meetings, related to the Contract, shall be in English.

Any information that a Party considers significant enough to bring to the attention of the other Party, shall be deemed correctly communicated if exchanged in writing (e-mail suffices) between the two persons in charge of the general organization of the Contract.

Any contract-related request – of technical or any other nature – directed by SCK CEN to the Contractor shall be adequately responded to within five Business Days.  If such request cannot be answered within this lead time, e.g. due to a technical question requiring additional time to be answered, the Contractor shall at least communicate (within this lead time) when SCK CEN will receive the answer.

If the Contractor anticipates any delays or difficulties in meeting the schedule, planned deliveries or any other milestone within its offer, they must promptly notify SCK CEN.

Contract Management

Progress Dashboard

The Contractor shall implement a digital dashboard giving SCK CEN a snapshot up-to-date information on the status and progress of the Contract.  The information shall be continuously (at least monthly) updated with the latest information.  The Contractor shall produce and submit monthly progress reports to SCK CEN at least three Business Days prior to the monthly progress meeting.  If comments or revisions arise during the progress meeting, the Contractor shall issue an updated version five business days after the meeting.  To this end, SCK CEN shall provide access for the Contractor to SCK CEN’s designated document management system.

The dashboard shall, as a minimum, include the following:

- A concise summary of the Contract progress

- Updated open-action-register.

- Work completed since the last update of the dashboard including encountered difficulties and improvement proposal.

- Work scheduled until the next update of the dashboard

- Monitoring of the schedule

- Updated issue register, and any other points-of-attention identified during the performance of the Contract

- Updated Change register

- Updated non-conformity register

- Updated Risk register

In the offer, the Applicant shall include a concise description of the dashboard as well as the underlying management processes. This description must include sufficient detail to demonstrate compliance with the requirements.

Meetings

Meetings will take place at either of below locations:

- The Contractor’s premises.

- SCK CEN: Boeretang 200, 2400 Mol, Belgium or Avenue Hermann-Debroux 40, 1160 Brussels, Belgium.

- Any other location mutually agreed upon by the Contractor and SCK CEN, such as the premises of the deliverable’s component Contractors.

- In audio or video conferencing.

The Contractor shall ensure that all relevant information for these meeting is made available to SCK CEN at least three Business Days in advance including, but not limited to, meeting agenda, reports, and presentations.  The Contractor shall draft the minutes of these meetings and submit them to SCK CEN for review and approval within 5 Business Days following the meeting.

Travel expenses are paid by the party who travels.

Progress Meetings

The Contractor shall organize Progress meetings between the Contractor and SCK CEN at least monthly.

Milestone Meetings

Milestone Meetings shall be held at least for the following milestones, organized by the Contractor:

- Kick-Off meeting (M11)

  - This meeting is a “face-to-face” meeting to be held SCK CEN.

- Conceptual Design Review meeting

- Detailed Design Review meeting

- Installation review meeting in preparation for commissioning

- Provisional Acceptance Meeting/Contract Performance Closure meeting.

  - This meeting is a “face-to-face” meeting to be held at SCK CEN.

Technical Review Meetings

Technical Review Meetings (TRM’s) with the necessary stakeholders shall be held to define the technical baseline and identify any evolutions between reviews.

Risk Assessment and Risk Management Plan

The Applicant shall submit a preliminary Risk Assessment as part of their offer.  It shall contain all risks with a severity that are bound to compromise the successful completion of the Contract either in terms of schedule, budget, or technical requirements, irrespective of probability.

Based on the preliminary Risk Assessment, the Applicant shall submit a preliminary Risk Management Plan as part of their offer.  It shall present a top-level view of the mitigation strategy that the Applicant shall implement during contract execution, for all the risks that have been identified as unacceptable.

During contract execution, the Contractor shall detail, complete, and continuously maintain the Risk Assessment and update the Risk Management Plan accordingly.  The Contractor shall continuously monitor, identify, and document any new risks that might threaten the successful completion of the Contract in any way.  The Contractor shall duly implement the mitigation strategy in accordance with the Risk Management Plan.

Factory Access

During the performance of the Contract, SCK CEN and/or its representatives shall have access during normal working hours to (all) the location(s) where (part of) the Contract is being performed (including Contractor’s and Subcontractors' premises).  The Contractor shall be notified of any site visit at least five Business Days in advance.

General Quality Assurance and Control

Quality Assurance

The implementation, verification, and documentation of the obligations defined in this section are specified in Sections 3.9–3.15.

General requirements

The Contractor shall implement and maintain a Quality Management System compliant with ISO 9001 for all activities under this Contract;

A review and/or approval by SCK CEN shall never entail (provisional) acceptance or a release of responsibility vis-à-vis the Contractor in any way.

Quality Management System

Any Subcontractor shall also be ISO 9001 certified for their scope of work by a nationally accredited body. In absence of an ISO 9001 certified QMS, an equivalent system may be accepted after written approval from SCK CEN.  If deemed necessary, SCK CEN may request an audit as foreseen in section §7.1.8.

The Contractor shall inform SCK CEN of any change in certification during execution of the Contact.

Quality Assurance Program

Quality assurance and control activities, including QAP, MIP, inspections, and conformity assessment, shall be implemented in accordance with Sections 3.9–3.16.

The inspections, measurements, and testing activities described in the Contract are mandatory but comprise only the minimum required.  These activities are not intended to supplant any control, measurement, examination, inspection, or test usually performed by the Contractor to ensure the quality of the product.

Qualification of personnel

The Contractor shall ensure that all personnel involved in the performance of the Contract is qualified and trained to the required competencies to deliver results complying with SCK CEN requirements and specifications.  Special training and qualifications are specifically required for personnel responsible for welding and any on site rigging activities.

The Contractor shall keep records of personnel qualification and make them available to SCK CEN free of charge upon simple request.

The Contractor shall ensure that all personnel who have direct contact with SCK CEN can understand as well as express themselves fluently in English, both orally and in writing.

Document Retention and Submission Requirements

The Contractor shall retain all documents created under the Contract for a minimum period of ten (10) years, or for the duration required by applicable law, whichever is longer.

All documents submitted to SCK CEN shall:

  - be identified by a unique document code, version number, and document title.

  - include a reference to the Contract unless the document was created independently of the Contract.

  - be version-controlled and include a change log listing the modifications applied in each revision.

  - be reviewed and approved by competent and authorized personnel prior to submission to SCK CEN.

  - be submitted in digital format, compatible with commonly available application software for Microsoft Windows OS and suitable for transmission via the internet.

Change Management

Proposals for change to the project, its scope of work and/or previously approved deliverables, either initiated by the Contractor or by SCK CEN, shall be analysed and documented (in a “Change Request”) by the Contractor and submitted for approval to SCK CEN.

A Change Request shall at least contain following information:

  - the initiator of the change

  - the justification for the change

  - the impact of the change (on product and/or (related) service(s),

  - safety,

  - risks,

  - contract price and schedule),

  - the description of the change and the plan of implementation.

The Contractor shall include the Change Request template in annex to the QAP.

Only Change Requests approved by SCK CEN may and shall be implemented.

A Change Request having a budgetary impact on the Contractor shall form the basis for a Variation Order.  In such event, the Change Request shall be considered as approved when the Variation Order is issued by SCK CEN.

The Contractor shall create and maintain a Change Register, accessible to SCK CEN, in which all Change Requests shall be logged, including at least:

  - a unique identifier, title, date of issuance,

  - monetary impact,

  - impact on the Contract schedule, and information about the status of (vi) the decision (potential, pending, approved, withdrawn, or disputed) and (vii) the implementation.

  - Deviations from the specifications defined in the Contract, that were not explicitly authorized by SCK CEN in advance in writing, shall be treated as Non-Conformities.

Non-Conformity Management

A Non-Conformity is defined as any non-compliance with, or deviation from, any of the requirements and/or conformity criteria set forth in the Contract or approved Change Requests.

The Contractor shall have a process in place for managing Non-Conformities that arise during the performance of the Contract, including receiving and processing notifications of Non-Conformities from SCK CEN and/or third parties (such as its Contractors or Subcontractors).

In case of a Non-Conformity, the Contractor may not ship, or shall recall at its own risk and expense, the impacted supply.  Any steps of the Contract execution, which are (potentially) affected by the Non-Conformity, shall be put on hold.

The Contractor shall notify SCK CEN in writing of any such Non-Conformities by means of a Non-Conformity Report (NCR).  An NCR shall be submitted to SCK CEN as soon as reasonably possible after a Non-Conformity is identified.

The NCR shall cover at least the following aspects:

  - Detailed description of the Non-Conformity.

  - Identification of all potentially affected deliverables.

  - Identified (root) cause(s) including verification thereof.

  - Proposed corrective actions including their anticipated effectiveness.

  - Proposed reoccurrence prevention plan (if applicable).

  - The Contractor shall include the NCR template in annex to the QAP.

  - The NCR shall be submitted to SCK CEN for approval.  SCK CEN shall be entitled to reject the solution(s) proposed by the Contractor in case SCK CEN deems the solution not useable given the circumstances.

The Contractor shall perform the necessary actions to correct the Non-Conformity (in accordance with the SCK CEN approved NCR) at its own risk and expense.  Said necessary actions shall not only concern redoing (parts of) the manufacturing and/or its related processes (assembly, packaging, delivery, …) but shall also entail redoing all QA/QC activities associated therewith.  Next to that, if so, requested by SCK CEN, the Contractor shall moreover reimburse SCK CEN for the costs incurred by SCK CEN to have the FAT/SAT of the impacted items redone.

The Contractor shall keep SCK CEN duly informed about the progress of the implementation of the actions identified in the NCR and, if applicable, shall provide a revised schedule identifying the time impact of the implementation of said actions; the Contractor shall minimize the consequences on the schedule in any case.

    - At the specific request of SCK CEN, to avoid repetition of possible recurring Non-Conformities during the execution of the Contract, or when imposed by the Contractor's quality management system or the QAP, the Contractor shall carry out a root cause analysis of the Non-Conformity.  Such an analysis shall:

- be documented and submitted for approval to SCK CEN.

- include the identified Non-Conformity cause(s).

- propose an action plan to minimize the probability of a recurrence.

    - For actions taking more than 1 month, the Contractor shall provide a regular status report describing the result of implementation according to the due dates in the action plan.

    - Performing the root cause analysis and implementing any preventive/corrective actions arising therefrom, shall not give rise to any additional compensation for the Contractor.

Any Non-Conformities identified and reported by SCK CEN to the Contractor, as well as any other complaints received by the Contractor from SCK CEN, shall be treated as Non-Conformities and duly documented, investigated, and resolved according to the stipulations under this clause.

Neither the implementation of the procedure on Non-Conformity management, nor the approval by SCK CEN of a Non-Conformity Report, shall waive or reduce the Contractor’s responsibility, according to the relevant stipulations of the Contract, to indemnify and hold SCK CEN harmless against all losses, damages, and costs (e.g. due to delay on the schedule) arising from such Non-Conformity.

Audits

SCK CEN shall be entitled to carry out, or to have carried out by a third party on its behalf (procured at SCK CEN’s own cost), an audit of Contractor/its Subcontractor’s premises, equipment, procedures to assess the ability of Contractor/Subcontractor to comply with the requirements of this document and the Contract.  SCK CEN may request such audit when at least one of the following conditions is met:

    - to qualify a Contractor/Subcontractor which is not ISO 9001 certified.

    - to address performance issues.

SCK CEN shall inform the Contractor in advance of the audit and shall take all necessary steps not to unduly interfere with the performance of Contractor’s business operations.  SCK CEN shall provide an audit report within two weeks of completing the audit.  The Contractor shall respond within two weeks with an action plan to address the identified Non-Conformities.

Quality Control

General requirements

- The Contractor shall perform the quality control according to best practices, as generally recognized, as well as, as assessed based on his internal ability and prior experience.

The Contractor shall be fully responsible for the quality of the deliverables and documentation produced and the quality of all components, materials, and services procured by the Contractor.

The Contractor shall ensure that the Contract is performed in accordance with all applicable regional, national, and international laws, regulations and industrial codes and standards and Good Industry Practices.

Additionally, to ensure compliance with the requirements outlined in this document, the QAP shall include at least the qualification and validation requirements specified in this document.

Declaration of conformity with all requirements

Together with the delivery, the Contractor shall submit to SCK CEN a Declaration of Conformity certifying that all the requirements have been met.  Such declaration shall include at least the following information:

    - Identification of the deliverable, including the purchase order reference no. and Contract reference.

    - A list of approved changes, waivers, or deviations from the specifications.

    - Such declaration shall be dated and signed by a duly authorized representative of the Contractor responsible for quality assurance as shown in the approved QAP.

Acceptance and Warranty

During the warranty and after-sales period, the Contractor shall maintain application of its ISO 9001 Quality Management System to all services provided under this Contract, including maintenance, repairs, modifications, and upgrades.  Non-conformities, changes and configuration updates during the warranty period shall be managed according to the same Non-Conformity and Change Management processes as applied during the project phases.

Provisional Acceptance

A Provisional Acceptance Certificate shall be issued by SCK CEN for each deliverable (together with the required documentation), provided that no shortcomings are identified during the provisional acceptance.

The provisional acceptance shall be subject to:

    - the successful completion of the SAT and

    - all identified Non-Conformities (e.g. documentation lacking) having been duly corrected by the Contractor.

Warranty Period

The Warranty Period for the CRYOPLANT shall be three (3) years from the date of the issuance of the Provisional Acceptance Certificate.  In-warranty repairs and/or replacement parts shall be warranted for at least one (1) year after execution, or for the unexpired portion of the original Warranty Period of the CRYOPLANT, whichever is longest.  Notwithstanding the foregoing, the Warranty Period is suspended for the duration between formal notice by the Contracting Authority to the Contractor on the defect and resolving of said defect by the Contractor.

If the Contractor fails to fulfil its obligations under the warranty, so that final acceptance cannot take place at the scheduled time, the Warranty Period shall be automatically extended, without any right to compensation for the Contractor, until final acceptance takes place.

Warranty Conditions

During the warranty period, the Contractor shall at its own risk and expense remedy any outstanding issues, as well as any shortcomings and defects that were not visible during the acceptance tests.

The Contractor’s methods of solving a warranty issue shall always need to be approved in advance by SCK CEN. SCK CEN reserves the right, at its sole discretion, to not allow for repair and to demand replacement of a defective item.

In case the warranty work needs to be performed at SCK CEN, the Contractor shall consider and comply with SCK CEN’s instructions relating to working hours, access, ..., without being entitled to any additional compensation.

The Contractor’s warranty obligation shall not apply:

    - to normal wear and tear of the QPLANT, as well as any associated consumables.

    - to defects of which the Contractor is notified after the Warranty period, unless SCK CEN can demonstrate that such defect has arisen before the end of the Warranty period in which case such defect shall fall under the warranty obligation.

    - to failures or defects which the Contractor can substantiate are due to alteration, misapplication, inappropriate use in view of the conditions of use as outlined by the Contractor (if any are provided), and/or maintenance not carried out according to the Contractor’s nominal conditions as set forth by the Contractor, lack of trained maintenance personnel (other than the Contractor’s personnel), operation above rated capacities either intentional or otherwise, or physical damage caused by persons other than the Contractor’s personnel.

During the warranty period, the Contractor shall execute repairs and/or replacements without undue delay at the Contractor’s risk and expense.  SCK CEN may request warranty service during non-normal working hours or for services excluded from the warranty coverage as defined herein, provided that SCK CEN shall pay the reasonable overtime premium portion of the non-normal hours worked or the normal service charge, respectively.

In-warranty repairs and/or replacement parts shall be warranted for at least one year after execution, or for the unexpired portion of the original warranty period of the deliverable, whichever is longest.  Notwithstanding the foregoing, the warranty period is suspended for the duration between formal notice by SCK CEN to the Contractor on the defect and resolving of said defect by the Contractor.

If the Contractor fails to fulfil its obligations under the warranty, so that final acceptance cannot take place at the scheduled time, the warranty period shall be automatically extended, without any right to compensation and/or remuneration for the Contractor, until final acceptance takes place.

The Contractor shall keep a register of all interventions that the Contractor performs during the warranty period which can be always consulted by SCK CEN.  If SCK CEN can demonstrate a trend of failure occurring during the warranty period, which is not attributable to any inappropriate use of the equipment, this will be considered as a deficiency, and the Contractor shall be liable to replace at his own risk and expense the affected item

In addition to the above rights, SCK CEN shall be entitled to full compensation for all damages incurred in view of these outstanding issues, shortcomings, and/or defects during the warranty period for which the Contractor is responsible.

The warranty as described in this section shall in no way constitute a restriction on the applicable Belgian statutory regulations on hidden defects.

Final Acceptance

Initial acceptance occurs after the successful completion of the Warranty Period, at the written request of the Contractor, on the condition that all defects, attributable to the Contractor, regardless of whether they have been identified in the Provisional Acceptance Certificate or during the Warranty Period, have been duly resolved by the Contractor.  If the conditions are met, a Final Acceptance Certificate will be issued by SCK CEN within 10 Business Days after receipt of the Contractor’s written request in this respect.

Appendix

Cooling Power for Cool-down

During a sequential cooldown of the 50 K masses when the magnetic shields temperatures are below 70 K, the cool down of the cavities and couplers from the Thermal Shield temperature to 4.5 K can start.

When the cavities reach the liquid helium temperature (4.5 K Static), the liquid filling of the helium baths can start.

Simplified cooling model

Figure 14 Simplified cooling model

System Mass Summary

The QPLANT cryogenic system consists of two main cooling stages: the 50K stage and the 2K stage.  The following table provides the total mass of each stage, including all structural and functional components.

Table 24 System mass

| Material | 2 K Stage kg (fraction) | 50 K Stage kg (fraction) |
| --- | --- | --- |
| Stainless Steel (SS) | 4 868 (0.3939) | 1 007 (0.0936) |
| Copper (Cu) | 0 (0) | 7 597 (0.7065) |
| Aluminium (Al) | 0 (0) | 2 149 (0.1998) |
| Nickel (Ni) | 2 730 (0.2210) | 0 (0) |
| Niobium (Nb) | 2 808 (0.2273) | 0 (0) |
| Titanium (Ti) | 1 950 (0.1578) | 0 (0) |
| Stage Totals | 12 356 kg | 10 753 kg |

Note: These masses represent the total system mass including all materials (stainless steel, copper, aluminium, niobium, titanium, and nickel).  The mass-weighted average specific heat and enthalpy values shall be used for cooldown calculations.

Static heat load as a function of temperature

| Heat load ID | Type of heat load | Formula |
| --- | --- | --- |
| HLcond 50 K-2 K | Static | -2.4T1T2λSS304/316-NISTTdT |
| HLrad 50 K-2 K | Static | 1.49E-05*T14-T24 |
| HLcond 293.15 K-50 K | Static | -0.87T1T2λSS304/316-NISTTdT |
| HLrad 293.15 K-50 K | Static | 4.15E-07*T14-T24 |

Enthalpy data of metal at various temperatures

Table 25 Weighted Average Enthalpy Data (1K - 300K)

| Temperature (K) | 2K Stage Enthalpy (J/kg) | 50K Stage Enthalpy (J/kg) |
| --- | --- | --- |
| 1 | 0.0 | 0.0 |
| 2 | 0.6 | 0.1 |
| 3 | 1.2 | 0.2 |
| 4 | 2.2 | 0.4 |
| 6 | 4.9 | 0.9 |
| 8 | 9.9 | 2.7 |
| 10 | 16.0 | 4.9 |
| 15 | 40.3 | 17.6 |
| 20 | 84.2 | 46.5 |
| 25 | 159.2 | 107.9 |
| 30 | 280.4 | 218.5 |
| 35 | 465.4 | 401.0 |
| 40 | 729.3 | 670.7 |
| 50 | 1534.9 | 1518.9 |
| 60 | 2685.0 | 2810.3 |
| 70 | 4173.2 | 4547.0 |
| 77 | 5409.5 | 6017.7 |
| 80 | 5982.0 | 6710.4 |
| 90 | 8073.3 | 9248.1 |
| 100 | 10413.9 | 12096.5 |
| 120 | 15695.1 | 18566.3 |
| 140 | 21679.0 | 25911.4 |
| 160 | 28262.6 | 33951.3 |
| 180 | 35377.0 | 42530.5 |
| 200 | 42937.0 | 51512.2 |
| 220 | 50797.2 | 60789.0 |
| 240 | 58829.0 | 70288.9 |
| 260 | 66978.2 | 79970.8 |
| 280 | 75256.0 | 89822.2 |
| 300 | 83753.4 | 99870.3 |

Control Systems

Instructions for GQRC

Table 26 Instructions for GSHRC

| Req. | Specific instruction |
| --- | --- |
| GSHRC-1 | Applicable. Software hardware and firmware are deliverables. |
| GSHRC-2 | Applicable. Final Software Architecture shall be delivered as part of DD-4. |
| GSHRC-3 | Applicable. Final System Interlock Diagram shall be delivered as part of DD-4. |
| GSHRC-4 | Applicable. Final Interface Design Description shall be delivered as part of DD-4. |
| GSHRC-5 | Applicable. Datasheets shall be delivered as part of DD-8. |
| GSHRC-6 | Applicable. A Release Note shall be delivered as part of DD-10. And after any change after acceptance. |
| GSHRC-7 | Applicable. An Installation Instructions shall be delivered as part of DD-8. |
| GSHRC-8 | Applicable. A Test Plan shall be delivered as part of DD-4. |
| GSHRC-9 | Applicable. |
| GSHRC-10 | Applicable. An Interface Test Plan shall be delivered as part of DD-4 and report shall be delivered as part of DD-10. |
| GSHRC-11 | Applicable. An Interface Simulator shall be delivered as part of DD-4. See paragraph Software Change Management for more details. |
| GSHRC-12 | Applicable. A Test System Description shall be delivered as part of DD-4. |
| GSHRC-13 | Applicable. An Interlock Test Plan shall be delivered as part of DD-4. |
| GSHRC-14 | Applicable. An Interlock Test Report shall be delivered as part of DD-10. |
| GSHRC-15 | Not Applicable. Not a deliverable. See paragraph Software Change Management for more details. |
| GSHRC-16 | Applicable. Description of the used internally used test system required by applicant. |
| GSHRC-17 | Granting a license for background materials is applicable and shall be delivered as part of DD-11 |
| GSHRC-18 | Applicable. Delivery of the background materials shall be done before DD-11 |
| GSHRC-19 | Updates of Background materials are applicable up to the end of the Warranty period. |
| GSHRC-20 | Granting a license for foreground materials is applicable and shall be delivered as part of DD-11 |
| GSHRC-21 | Applicable. Delivery of the foreground materials shall be done |
| GSHRC-22 | Updates of foreground materials are applicable up to the end of the Warranty period. |
| GSHRC-23 | Applicable. Restrictions on use of specific open-source licenses for SW/HW Materials |
| GSHRC-24 | Applicable. Restrictions on open-source licenses for combined work |
| GSHRC-25 | Applicable. Inventory must be provided with each Release Note |
| GSHRC-26 | Applicable. Sublicense(s) for intended use |
| GSHRC-27 | Applicable: warranty |
| GSHRC-28 | Applicable: Escrow |
| GSHRC-29 | Applicable. Updates of Escrow Materials must be promptly deposited if changes occur. |
| GSHRC-30 | Applicable. Upkeep of escrow is required, and fees are paid by SCK CEN. |
| GSHRC-31 | Applicable. Description of secure software development must be provided. |
| GSHRC-32 | Applicable. Delivery of secure software is required with no known exploitable vulnerabilities. |
| GSHRC-33 | Applicable. Default configuration must be secure. |
| GSHRC-34 | Applicable. Description of a default configuration must be provided. |
| GSHRC-35 | Applicable. Description of vulnerability management process must be provided. |
| GSHRC-36 | Applicable. Description of policy for Coordinated Vulnerability Disclosure must be provided. |
| GSHRC-37 | Applicable. Known Vulnerabilities must be listed in Release Notes. |
| GSHRC-38 | Applicable. Distribution of patches/updates to mitigate Vulnerabilities is required. |
| GSHRC-39 | Applicable. Description of software defects process must be provided. |
| GSHRC-40 | Applicable. Known software defects must be listed in Release Notes. |
| GSHRC-41 | Applicable. Distribution of patches/updates to address software defects is required. |

Control Architecture details

The following table expands on details as per Figure 9.

Table 27 Control Architecture details

| No. | Name | Description |
| --- | --- | --- |
| 11–19: Local Engineering and Control Stations |  |  |
| 11 | Engineering Station | A dedicated workstation for running the engineering tools in commissioning stage. |
| 111 | Engineering Tool | A dedicated engineering software for configuring, troubleshooting, or programming the QPLANT:CIS during commissioning phase. |
| 12 | Local Operator Station (HMI) | A touchscreen placed near the cryogenic plant for direct operator interactions, real-time control, and monitoring. |
| 121 | QPLANT HMI | Local HMI |
| 13 | Warm Compressor Station PLC | A PLC in charge of warm compressor processes and associated subsystems in the cryogenic plant. |
| 131 | WCS Software | The software component or logic running on the Warm Compressor Station PLC. |
| 14 | ColdBox PLC | A PLC handling cold-related processes (cold box, vacuum insulation, other sub-circuits) in the QPLANT. |
| 141 | CB Software | The software controlling the cold box, vacuum insulation, ... |
| 143 | IVAC Software | The software dedicated to insulation vacuum, or auxiliary cold systems. |
| 15 | PN-PN Coupler | A Profinet-to-Profinet coupler device bridging two separate PN networks or segments in ICS/plant architecture. |
| 151 | Interface Definition | The definition of the interface used for controlling and monitoring the QPLANT. |
| 20–29: Aggregation and System PLCs |  |  |
| 20 | Concentrator PLC | A PLC responsible for system level control, integrating the QPLANT with the MCS Navigator and aligning consumers with production plant. |
| 201 | QCELL_BROKER Software | A software component that mediates the QCELL consumers with the QPLANT production. |
| 202 | Plant Control and Monitoring | A software component that instructs the QPLANT operation to align with the accelerator needs. |
| 204 | OPC-UA Server | A server implementing OPC-UA for data exchange with MCS Navigator. |
| 21 | QVE Local Controller | A PLC for controlling and monitoring the end valvebox. |
| 211 | QVE Control Logic | Logic for controlling the end valvebox. |
| 22 | QCELL_Controller | A PLC for controlling and monitoring cryogenic cells. |
| 221 | QCELL Control Logic | A software component implementing the logic for the QCELL control. |
| 30–39: Networks and Communication |  |  |
| 30 | MIT Network | Networks |
| 31 | MIS Network | A dedicated fieldbus network for safety related communication. |
| 32 | Local Fieldbus Network | A fieldbus network in scope of Contractor for interconnecting local devices (PLCs, sensors, ...) |
| 33 | Local Fieldbus Network | A fieldbus network in scope of ICS for interconnecting local devices (PLCs, sensors, ...). |
| 34 | QPLANT Aggregation Ntw | The aggregation network serves as an intermediary between the MIT backbone and the Plant. |
| 40–49: Clients |  |  |
| 41 | Zero Client | MIT backbone upper-level network. |
| 50–59: Interlocks and Safety |  |  |
| 50 | MIS Interlock System | A system responsible for global personal and machine protection. |
| 501 | Interlock Controller | A PLC controller responsible for integrating relevant QPLANT interlocks with the MIS system. |
| 70–79: Deployment and Services |  |  |
| 70 | MCS Deployment Service | A deployment service for QPLANT, used to distribute or update software components. |
| 701 | Deployment Tool | Tool used for deploying new software versions to the QPLANT:CIS. |
| 72 | MIT Services | Global IT services like NTP, Authentication, etc. |
| 721 | NTP Service | A network time protocol service for time synchronization across ICS or QPLANT systems. |
| 73 | MCS Services | Control System shared services like the Navigator, Archiving etc. |
| 731 | Archiver | A data historian or archiving service used to record historical process data for the accelerator and the QPLANT. |
| 80–89: Visualization and Clients |  |  |
| 80 | Zero Client | Used for visualizing MCS Navigator, the zero client displays the user interface generated by the server. All processing, data storage, and updates occur centrally. |
| 90–99: Servers and Supervisory Systems |  |  |
| 90 | Server (Cluster) | Server cluster based on KVM (for Kernel-based Virtual Machine) full virtualization solution for Linux on x86 hardware. |
| 711 | Navigator | The project wide SCADA system for controlling/monitoring the accelerator and the cryogenic processes at a higher supervisory level. |
| 7111 | QPLANT | A control panel or interface for the QPLANT. |
| 7112 | QCELLPanel | A control panel or interface for a cryogenic cell. |

Applicable Documents

SCK CEN is providing the required information necessary for the performance of the Contract as outlined in this Addendum.  The level of maturity provided is that necessary for the Applicant to provide and offer.  Within Contract execution, SCK CEN may provide updated versions of the applicable documents listed below.

Table 28 Applicable Documents (AD)

| Document name | Reference |
| --- | --- |
| D2.1 Preliminary Design | SCK CEN/81777062 |
| SCK CEN Auxiliary Building | SCK CEN/89811518 |
| Safety Plan (for LCP4 onwards) | SCK CEN/56057080 |
| General Specification for Steel Piping Materials | SCK CEN/81912295 |
| General Software and Hardware Requirements for Contractors | SCK CEN/55310227 |
| Requirements for Electrical Equipment Included in Package Plants | SCK CEN/81913364 |
| EMC Guidelines | SCK CEN/81913579 |
| SCADA HMI Guideline | SCK CEN/53012565 |
| Technical Specification for Control Valves | SCK CEN/81912936 |
| Technical Specification for Instruments | SCK CEN/89816164 |
| Painting and coating specification | SCK CEN/81913862 |
| Technical Specification for Plate Heat Exchangers | SCK CEN/81912893 |
| MIT Interface Catalogue | SCK CEN/81912045 |
| Technical Specification for Shop Fabricated Tanks | SCK CEN/81913369 |
| TS Of Manual and Motor Operated Metallic Valves | SCK CEN/81912050 |
| MIS Slow Interlock interface - (applies also to non-safety digital communication) | SCK CEN/48282970 |
| Analog Signals: 4-20mA (NAMUR NE43) |  |
| MCS architecture | SCK CEN/38585071 |
| MIS architecture | SCK CEN/39550252 |
| MIT architecture | SCK CEN/39553304 |
| MCS Interface Catalogue | SCK CEN/48276492 |
| Slow interlock interface document | SCK CEN/48282970 |
| MIT Interface Catalogue | SCK CEN/55564083 |
| MCS Secondary Interface Catalogue: Profibus DP | SCK CEN/48483448 |
| MCS Slow Control OPC UA Interface | SCK CEN/56163474 |
| MCS Slow Control PROFINET Interface | SCK CEN/55190851 |
| General Software and Hardware Requirements for Contractors | SCK CEN/55310227 |

- Operational and maintenance expected needs over a defined period of 5 years including:

  - Preventive and corrective maintenance activities (including planned replacements based on LRU lifetime and respective component MTBF and reliability data, software updates, calibration, compliance re-certifications, and energy efficiency optimization.  Specific assumptions apply for forecasted OPEX:

- Nitrogen cost: 250€/ton

- Electricity cost: 142 €/MWh

- Helium inventory: 250 €/kg (annual losses to be defined the Applicant)

“4.5 K Standby” refers to saturated helium near 1 bara (~4.2–4.3 K), not a pressurized 4.5 K supply.  The label is retained for consistency with system mode naming.