SCK CEN Ref.:	SCK CEN/ xxx xxxx

Third Party Ref.:

QPLANT - Granting Phase

# MAC helium supply (dewar) and recovery from experiment

Tender reference: 2024-XXX-AF

SBS level: MINERVA-ATS-QSYST-QPLANT-QRB

Table of Contents

MAC helium supply (dewar) and recovery from experiment	1

1	“Gold Finger” Experiment Concept	2

1.1	Principle of Operation	2

1.2	Key points:	2

2	Interface Definition and Requirements	2

2.1	Interface Location	2

2.2	Helium Usage and Recuperation (from CR1299)	2

2.3	Helium Purity	3

2.4	Pressure and Flow Ranges	3

2.5	Client (User) Responsibilities	3

2.6	Contractor (System Designer) Responsibilities	4

2.7	Procedures & Preparation for QPLANT Integration	4

3	Options for Recovery and Warm‐Gas Management	4

3.1	Normal Operation	4

3.2	Upset or High‐Flow Condition	4

3.3	Pumped Return (Sub‐Atmospheric or Low‐Pressure Helium)	4

3.4	System Purification & End‐of‐Pipe Clean‐Up	5

3.5	Periodic Vent/Purge for Idle Periods	5

4	Proposed Bill of Materials (BOM)	5

4.1	Piping & Insulation	5

4.2	Valves & Flow Control	5

4.3	Instrumentation	5

4.4	Helium Purifier / Filter Skid	6

4.5	Warm Gas Management	6

4.6	Structural & Support Components	6

4.7	Control & Integration	6

4.8	Documentation & Commissioning	6

4.9	Vent/Purge Equipment (Add-On)	6

5	References & Design Considerations	7

5.1	Mechanism / Process Description (Step‐by‐Step)	7

6	Comprehensive Requirements Table	9

# “Gold Finger” Experiment Concept

## Principle of Operation

A “Gold Finger” experiment uses a thermally conductive rod or “finger” immersed in a liquid helium bath. By letting the helium evaporate at (or near) atmospheric pressure, the rod (and any attached sample or instrumentation) stays at helium boiling temperature (~4.2 K). This setup allows:

- Stable 4.2 K without sub-coolers or sub-atmospheric pumping.

- Latent heat of vaporization of helium to absorb heat from the experiment.

## Key points:

- Liquid helium off‐take: Drawn from a liquid supply source (e.g., a main Dewar, a cryoplant storage vessel, or a helium distribution line).

- Evaporation Cooling: The liquid helium boils off at 1 atm (or slightly above) inside the experiment. Heat is absorbed in the latent heat of vaporization, maintaining a stable low temperature.

- Gaseous Helium Return: The boiled-off helium is routed back via a “return” (low-pressure) line to the helium compressor suction or a recovery/purification system.

This approach guarantees a stable 4.2 K environment (assuming relatively low heat load and a stable supply of liquid helium) without requiring sub-coolers or sub-atmospheric pumping.

# Interface Definition and Requirements

Below is an overview of responsibilities and technical requirements for an external user (the Gold Finger experiment) connecting to a helium cryoplant (QPLANT) or distribution network (QCELL). It includes the interface location, helium purity demands, pressure/flow ranges, and roles of both the client (user) and the contractor (system designer).

## Interface Location

- Physical Boundary: The southeast wall of the Coldbox Room, after any ambient gas heaters or existing facility piping.

- The user’s scope starts at the tie‐in flanges (or welded connections) to the main LP return line (~300 mm OD) and any associated control/instrumentation lines.

(Req.#2, Tie‐In Location & Physical Boundary, “Contractor shall connect the user return piping to QPLANT at the southeast wall of the coldbox room on the 300 mm main LP line…”)

## Helium Usage and Recuperation (from CR1299)

- Typical Liquid Helium Consumption for PTF experimental setups:

  - 150 to 200 litres for initial cooldown.

  - 40–50 litres/day to keep the temperature at ~4.2 K.

- NFS shall provide dewars and manage the transport. ATS provides (via QPLANT @ QRB) a liquid helium dewar filling terminal point for use in MAC PS.

- Helium‐tight recuperation lines must return evaporated helium gas to the cryogenic supply system.

- Return line pressure must remain above 1000 mbar to avoid contamination risk. No sub-1000 mbar return is allowed.

- Return line must only include non‐contaminated helium (no direct recovery or added purification is foreseen by ACR); if purity standards are not met, the user (NFS) is responsible for venting.

- ATS and NFS must agree on minimum acceptable gas composition (H₂O, O₂, N₂, etc.); any helium lost due to contamination or venting is the responsibility of MAC PS.

- A specific procedure (e.g. line conditioning, valve permissive, etc.) shall be developed by NFS and ACR to ensure that liquid helium removal does not affect the QPLANT’s reliability.

- Limited Operation Note: The experiment may only run 1 month per year (1/12). During the remaining 11 months, the line and associated equipment must be purged, dried, and maintained to preserve helium purity and readiness for the next operational cycle.

## Helium Purity

The cryoplant typically requires high‐purity helium (99.999+% or better). Allowable impurities: O₂ < 1 ppm, N₂ < 5 ppm; no particulate contamination or water vapor. The user must ensure their process does not introduce additional contaminants (oil, dust, water, etc.).

(Req.#1, Helium Purity Maintenance, “Contractor shall ensure that helium return gas purity does not exceed 1 ppm O₂ and 5 ppm N₂ under normal and upset conditions.”)

## Pressure and Flow Ranges

- Liquid Helium Supply: Typically, ~1.2–1.3 bar(a) saturated liquid from an external source.

- Gaseous Helium Return: Nominal return pressure: ~1.05 bar(a) at the compressor suction.

  - The line may see flow variations up to 100 g/s (S‐line design flow) and possibly short‐term up to 200 g/s (QVE or upset conditions).

(Req.#3, Nominal & Upset Flow Handling, “Contractor shall design the return line and associated control elements to manage a nominal 100 g/s and surges up to 200 g/s…”) (Req.#4, Return Line Suction Pressure Control, “Contractor shall incorporate a control valve or equivalent device to maintain compressor suction pressure at 1.05 bar(a) ±0.02 bar(a)…”)

## Client (User) Responsibilities

- Full return line from the experiment to the QPLANT boundary (including piping, insulation, valves, instrumentation, safety devices).

- Ensuring helium purity is not compromised (filtration, dryness, no atmospheric ingestion).

- Managing transient flows (start‐up, shutdown, upset, or quench scenarios).

- Providing local buffer/balloon tanks if needed to manage flow surges beyond QPLANT’s capacity (e.g., 200 g/s upsets).

- Guaranteeing that any helium returned meets agreed-upon purity specs, or else venting the gas.

- Managing Off-Line Periods: If the experiment is only operational 1 month per year, the user must plan thorough line conditioning prior to re-start, including purging, inert-gas blanketing, or dryness checks.

## Contractor (System Designer) Responsibilities

- Provide detailed specifications for:

  - Fluid conditions (pressure, temperature, purity).

  - Warm gas management components (valves, heaters, purifiers, instrumentation).

  - Recovery compressor or tie‐in to the existing helium compressor system.

  - Manifold design for normal operation vs. upset (S‐line at 100 g/s, surges to 200 g/s).

- Control strategy for stable pressure regulation (flow control valve, suction pressure regulation, etc.).

- Evaluate how upstream or downstream flows interact with QPLANT operation; propose solutions to maintain stability (e.g., small “ballast” volumes, control valve trim, rapid response flow control).

- Develop a Handling Procedure to define how to safely take liquid helium from the supply line and manage the return stream to QPLANT, including vent or purge steps prior to cooldown and after warm-up.

## Procedures & Preparation for QPLANT Integration

- Contractor shall document step-by-step instructions on how the line is to be cooled down, how helium is introduced, and how to manage the flow back into QPLANT. This includes any required pre-cool purging, verifying dryness, establishing valve permissive, and ramping up flow.

- Vent/Purge Steps: For times when the system is brought offline or prepared for maintenance, the contractor’s procedure shall outline how to vent or purge the line (e.g., with helium or inert gas) to ensure dryness and zero contamination.

- A final sign-off or checklist with QPLANT operators is recommended before any test or operational run.

# Options for Recovery and Warm‐Gas Management

## Normal Operation

- Evaporated Helium from the Gold Finger flows continuously into the low‐pressure return line (S‐line).

- Flow Control via a control valve or orifice, maintaining ~1 atm at the experiment.

- Pressure sensors tie into the QPLANT control system.

## Upset or High‐Flow Condition

- Excess Boil‐Off: Flow can exceed 100 g/s if a sudden heat load or an operational fault occurs.

- Buffer/Recovery Balloon: A flexible storage vessel can buffer short spikes, preventing over‐pressurization or compressor overload.

(Req.#5, Buffer/Surge Control, “Contractor shall provide a buffer tank (balloon) or surge management system to manage flow excursions (up to 200 g/s)…” )

## Pumped Return (Sub‐Atmospheric or Low‐Pressure Helium)

- If the helium must be drawn below 1.05 bar(a), or the plant suction is slightly sub‐atmospheric, a booster compressor or roots pump may be installed on the user side to ensure stable flow back to the main compressor.

- Upset or High‐Flow Condition: Flow can exceed nominal 100 g/s if a sudden heat load/fault.

- Buffer/Recovery Balloon can buffer short spikes to avoid over‐pressuring the LP line or overloading the compressor.

## System Purification & End‐of‐Pipe Clean‐Up

- Adsorber Beds / Getter Purification: Cold or ambient temperature adsorbers remove O₂, N₂, H₂O.

- Particulate Filtration: A fine filter (1–5 µm) prevents any debris from entering the cryoplant compressors.

(Req.#6, End‐of‐Pipe Purification, “Contractor shall install particulate filters (1–5 µm) and an adsorber bed or equivalent purifier…”)

- Automatic Purity Monitoring: In‐line O₂ analyser and dewpoint sensor to confirm dryness.

- Bypass / Regeneration Lines: If using adsorber beds, regeneration lines with heaters and vacuum pumps must be provided.

## Periodic Vent/Purge for Idle Periods

- When the Gold Finger line is not in operation (e.g., 11 months per year), it may be necessary to vent or purge the line to prevent contamination by ambient moisture or air.

- A venturi-based purge arrangement can be employed to create a low-pressure draw, ensuring all residual gases or moisture are removed.

- Contractor shall supply guidelines for frequency of purging, recommended purge gas (e.g., GHe or inert), and required dryness checks prior to the next cooldown.

# Proposed Bill of Materials (BOM)

Below is a typical (not exhaustive) BOM for integrating the Gold Finger user line into a helium cryoplant system:

## Piping & Insulation

- Liquid Helium Supply Line (e.g., 25–50 mm vacuum‐jacketed pipe if low flow).

- Return Gas Line (nominal 100 mm ID, or per flow requirements).

- Insulation: Vacuum‐jacketed or super insulated piping in cold sections to minimize heat leaks.

- Foam glass or cryogenic insulation on warm gas lines if temperature difference is large or to prevent condensation.

## Valves & Flow Control

- Isolation Valves (cryogenic valves at both supply and return sides).

- Control Valve (flow or pressure regulator on the return line to maintain ~1 atm at the experiment).

- Check Valve (Non‐Return Valve) to prevent backflow.

- Emergency Shut‐Off Valves as per safety codes.

## Instrumentation

- Pressure Transmitters (supply and return lines).

- Temperature Sensors (RTDs, Cernox, or silicon diode) at key points (LHe supply, evaporator zone, return line).

- Flow Meters (Coriolis or turbine) on the return line.

- Purity Analyzer (O₂ analyzer, dewpoint meter) near or at boundary.

(Req.#7, Monitoring & Control Integration, “Contractor shall provide pressure transmitters, temperature sensors, and flow meters on the user return line…” )

## Helium Purifier / Filter Skid

- Particulate Filter (1–5 µm).

- Adsorber Vessel (activated charcoal, molecular sieve, or getter material).

- Bypass Line & Regeneration connections, isolation valves.

## Warm Gas Management

- Buffer / Balloon Tank for flow surges (up to 200 g/s).

- Compressor or Booster Pump (if sub‐atmospheric or stable return is needed).

- Instrumentation & Control to manage transitions, keep suction ~1.05 bar.

## Structural & Support Components

- Pipe supports, brackets, vacuum jacket supports, expansion loops.

- Platforms or frames for purifier skids, instrumentation cabinets.

## Control & Integration

- PLC or DCS for local user control (monitoring flow, temperature, pressure).

- Interface Signals to QPLANT (interlocks, flow/pressure data).

- Emergency Shutdown logic integration with QPLANT’s safety system.

(Req.#8, Emergency Shut‐Off Valves (ESD), “Contractor shall install remotely operated emergency shut‐off valves on both the supply (LHe) line and the return line…” )

## Documentation & Commissioning

- Operations & Maintenance Manuals

(Req.#9, Operations & Maintenance Manuals, “Contractor shall deliver comprehensive O&M manuals… and conduct training…” )

- Integrated Commissioning

(Req.#10, Integrated Commissioning, “Contractor shall conduct integrated system testing… prior to final acceptance…” )

## Vent/Purge Equipment (Add-On)

- Vent/Purge Ports or Venturi Setup: For removing moisture or residual gases when the line is idle.

- Purge Gas Supply Line: Could be helium or inert, with pressure regulation to ensure safe line purge.

- Drain/Vent Valve Assembly: Valve arrangement to safely exhaust purge gas or residual helium to a vent stack or recovery manifold.

# References & Design Considerations

## Mechanism / Process Description (Step‐by‐Step)

- Liquid Helium Supply: Arrives at ~1.2–1.3 bar(a) from the QPLANT VIA local Dewar.

- Gold Finger Evaporation: The assembly, dipped into the helium bath or flow, evaporates helium to maintain ~4.2 K.

- Boil‐Off Gas: Gaseous helium passes through an orifice/control valve, regulating evaporation rate.

- Return Line: Gas enters the user’s 100 mm line, merging into the 300 mm LP line at the Coldbox boundary.

- Purifier (if inline): Contamination is removed (adsorbers, filters).

- Compressor Suction: Gas is compressed, purified, cooled, and liquefied in QPLANT, closing the loop.

# Comprehensive Requirements Table

| Req.# | Topic | Title | Requirement (Full Text) | Measurability | Reference Standards | Verification | Validation | Rationale |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Fluid Purity | Helium Purity Maintenance | “Contractor shall ensure that helium return gas purity does not exceed 1 ppm O₂ and 5 ppm N₂ under normal and upset conditions.” | O₂ analyzer readings (detection limit ≤0.1 ppm); periodic N₂ sampling (detection limit ≤1 ppm). | ISO 8573-1 (optional) | Review P&ID for analyzer placement; purifier design. FAT records for purifier performance. | 24-hour site acceptance test verifying O₂ <1 ppm, N₂ <5 ppm. Deliverable: Purity Log | Maintains cryoplant reliability by preventing contamination. |
| 2 | System Interface | Tie‐In Location & Physical Boundary | “Contractor shall connect the user return piping to QPLANT at the southeast wall of the coldbox room on the 300 mm main LP line…” | Physical location verified against official layout & line sizing. | N/A | On‐site inspection, as‐built drawings. | Commissioning test to confirm correct flow direction. Deliverable: Inspection Report | Ensures a clear boundary of responsibility, correct integration with existing infrastructure. |
| 3 | Flow Capacity | Nominal & Upset Flow Handling | “Contractor shall design the return line and associated control elements to manage a nominal 100 g/s and surges up to 200 g/s…” | Pressure drop calculations for flows at 100 g/s & 200 g/s; flow modelling or test data verifying line sizing. | ASME B31.3 (optional) | Pipe sizing calculations in design docs; flow simulation for transient conditions. | Operational test (step changes up to 200 g/s). Deliverable: Flow Capacity Test Record | Prevents over‐pressure, ensures stable operation for both user experiment and QPLANT. |
| 4 | Pressure Regulation | Return Line Suction Pressure Control | “Contractor shall incorporate a control valve or equivalent device to maintain compressor suction pressure at 1.05 bar(a) ± 0.02 bar(a)…” | Pressure sensor readings at return line inlet; real‐time monitoring. | IEC 61508 (optional) | Functional acceptance test of control valve system; instrumentation loop check. | Real‐time data logging during start‐up & steady state. Deliverable: Pressure Regulation Performance Report | Ensures stable suction conditions, avoiding compressor surge or choking. |
| 5 | Warm Gas Management | Buffer/Surge Control | “Contractor shall provide a buffer tank (balloon) or surge management system to manage flow excursions (up to 200 g/s)…” | Buffer tank volume sized for ≥60 seconds at 200 g/s; validated by worst‐case scenario. | N/A | Design review of tank sizing & MAWP; supplier data sheets for surge system. | Flow spike demonstration at commissioning. Deliverable: Surge Test Result | Protects cryoplant from sudden high‐flow transients; maintains system stability. |
| 6 | Filtration & Purification | End‐of‐Pipe Purification | “Contractor shall install particulate filters (1–5 µm) and an adsorber bed (or equivalent purifier) to remove moisture, oil, and other contaminants…” | Filter rating verified; dew point measurement in the return line. | ISO 12500 (optional) | Inspection of installed filter/purifier skid; OEM data for purifier performance. | Operational check of dew point & particulate count over 24 hours. Deliverable: Purification Test Report | Prevents compressor damage; upholds helium purity in liquefaction cycle. |
| 7 | Instrumentation | Monitoring & Control Integration | “Contractor shall provide pressure transmitters, temperature sensors, and flow meters on the user return line…” | Sensor accuracy (±0.5% FS); data logging in QPLANT PLC or DCS. | IEC 61298 (optional) | Instrument calibration certificates; FAT for I/O check with QPLANT system. | Functional test of data acquisition & alarms during commissioning. Deliverable: Instrumentation Integration Report | Ensures timely detection of abnormal conditions & effective operational control. |
| 8 | System Safety | Emergency Shut‐Off Valves (ESD) | “Contractor shall install remotely operated emergency shut‐off valves on both the supply (LHe) line and the return line…” | ESD valves must close fully within 5 seconds of emergency signal. | IEC 61511 (optional) | ESD function test (local & remote actuation); review valve sizing & response times. | Commissioning demonstration with simulated ESD event. Deliverable: ESD Function Test Report | Protects personnel & equipment from over‐pressure or hazardous releases. |
| 9 | Documentation & Training | Operations & Maintenance Manuals | “Contractor shall deliver comprehensive O&M manuals (including schematics, recommended maintenance) for all installed equipment and conduct training sessions for client staff.” | Delivery of final O&M docs ≥4 weeks before commissioning; training attendance logs. | N/A | Document review by client engineering; training sign‐off records. | On‐site training acceptance by client leads. Deliverable: O&M Manuals + Training Certificate | Ensures that client personnel understand the system & can minimize downtime. |
| 10 | Performance Test & Handover | Integrated Commissioning | “Contractor shall conduct integrated system testing (liquid supply, evaporation, return) to demonstrate compliance with flow, pressure, purity, and safety specs before final acceptance.” | Achieving O₂ <1 ppm, N₂ <5 ppm, stable flow ~100 g/s, ±0.02 bar on suction pressure, assessed over 48 hours. | N/A | Witness test by client/owner; signed test records vs. acceptance criteria. | System run at nominal load + upset test to 200 g/s. Deliverable: Commissioning & Acceptance Report | Ensures entire system performs per specs prior to handover. |