## Navigation
Sheet Name | Description
Requirements_Traceability_Matrix | Complete RTM with all requirements and traceability
SBS_Structure | System Breakdown Structure hierarchy
Summary_Statistics | Summary statistics and metrics
Requirements_by_SBS | Requirements organized by SBS levels
Requirements_by_Type | Requirements organized by type and category

## RTM
Requirement ID | Description | Full Description | SBS Level 0 | SBS Level 1 | SBS Level 2 | SBS Level 3 | Requirement Type | Category | Priority | Verification Method | Acceptance Criteria | Source Section | Parent Requirements | Child Requirements | Status | Rationale | Numerical Value
RTM-01 | The QPLANT shall be capable to operate uninterrupted in 2K mode for at least 90 consecutive days | The QPLANT shall be capable to operate uninterrupted in 2K mode for at least 90 consecutive days | QSYS | QPLANT | WCS |  | Performance | Operational | High | Test | Temperature condition: 2K; Value shall meet 90 | 3.2.1 Lifetime and annual maintenance schedule |  | RTM-02, RTM-03, RTM-04 | Active | Required for proper system functionality | 90 days
RTM-02 | The maintenance schedule shall take into account the following constraints: ≥ 6 months: ≤ 10 days in 2K standby; ≥ 1 year: ≤ 20 days in 4.5K standby; ≥ 5 years: ≤ 60 days in warm stop; ≥ 10 years: ≤ 120 days in warm stop | The maintenance schedule shall take into account the following constraints: ≥ 6 months: ≤ 10 days in 2K standby; ≥ 1 year: ≤ 20 days in 4.5K standby; ≥ 5 years: ≤ 60 days in warm stop; ≥ 10 years: ≤ 120 days in warm stop | QSYS | QPLANT | WCS |  | Functional | Maintenance | High | Test | Value shall meet 6 m; Value shall meet 10 ; Temperature condition: 2K | 3.2.1 Lifetime and annual maintenance schedule | RTM-01 |  | Active | Required for proper system functionality | Various time limits
RTM-03 | The QPLANT shall have a lifetime of at least 40 years | The QPLANT shall have a lifetime of at least 40 years | QSYS-PR | QPLANT | WCS |  | Design | Lifetime | High | Test | Value shall meet 40 | 3.2.1 Lifetime and annual maintenance schedule | RTM-01 |  | Active | Required to meet project lifetime objectives | 40 years
RTM-04 | The QPLANT shall support ≥ 50 warm-up/cool-down cycles (300 K ↔ 2 K) | The QPLANT shall support ≥ 50 warm-up/cool-down cycles (300 K ↔ 2 K) | QSYS | QPLANT | WCS |  | Functional | Operational | High | Test | Value shall meet 50 wa; Temperature condition: 300K; Temperature condition: 2K | 3.2.1 Lifetime and annual maintenance schedule | RTM-01 |  | Active | Required for proper system functionality | 50 cycles
RTM-05 | The QPLANT shall support the steady state operational scenarios: Warm Stop, Thermal Shield Standby, 4.5 K Standby, 2 K Standby, 2 K Operation | The QPLANT shall support the steady state operational scenarios: Warm Stop, Thermal Shield Standby, 4.5 K Standby, 2 K Standby, 2 K Operation | QSYS | QPLANT | WCS |  | Functional | Operational | High | Demonstration | Temperature condition: 4.5K; Temperature condition: 2K; Temperature condition: 2K | 3.2.2 Steady state operational scenarios |  |  | Active | Required for proper operational flexibility and system control | 5 scenarios
RTM-06 | The QPLANT shall support the scenario transitions given in Figure 6 | The QPLANT shall support the scenario transitions given in Figure 6 | QSYS | QPLANT | WCS |  | Functional | Operational | High | Test | Value shall meet 6 | 3.2.3 Transient operational scenarios |  | RTM-07, RTM-08, RTM-09, RTM-010, RTM-011, RTM-012 | Active | Required for proper operational flexibility and system control | Multiple transitions
RTM-07 | The QPLANT shall execute the transition using the capacity defined by the steady state scenarios. No additional capacity shall be added solely for acceleration of state transitions | The QPLANT shall execute the transition using the capacity defined by the steady state scenarios. No additional capacity shall be added solely for acceleration of state transitions | QSYS | QPLANT | WCS |  | Performance | Performance | High | Test | Compliance with requirement as specified | 3.2.3 Transient operational scenarios | RTM-06 |  | Active | Required to meet operational performance targets | Existing capacity only
RTM-08 | The QPLANT shall perform the cool-down of the QPLANT simultaneously with the cryogenic users (QCELL and QDIST static heat loads only) | The QPLANT shall perform the cool-down of the QPLANT simultaneously with the cryogenic users (QCELL and QDIST static heat loads only) | QSYS | QCELL |  |  | Functional | Operational | High | Test | Compliance with requirement as specified | 3.2.3 Transient operational scenarios | RTM-06 |  | Active | Required for proper system functionality | Simultaneous operation
RTM-09 | The QPLANT shall facilitate parallel cool down/warm up of all QCELLs. During cooldown and warm-up, cryomodules impose constraints: Magnetic shields must reach T < 70 K before cavities reach T < 10 K | The QPLANT shall facilitate parallel cool down/warm up of all QCELLs. During cooldown and warm-up, cryomodules impose constraints: Magnetic shields must reach T < 70 K before cavities reach T < 10 K | QSYS | QCELL |  |  | Functional | Operational | High | Test | Temperature condition: 70K; Temperature condition: 10K | 3.2.3 Transient operational scenarios | RTM-06 |  | Active | Required for proper system functionality | T < 70K and T < 10K
RTM-010 | The QPLANT shall facilitate an alternative cooldown in which only the thermal-shield (TS) circuit is cooled until their average temperature reaches 50 K. Subsequently the headers A–B and D–E are simultaneous cooled down | The QPLANT shall facilitate an alternative cooldown in which only the thermal-shield (TS) circuit is cooled until their average temperature reaches 50 K. Subsequently the headers A–B and D–E are simultaneous cooled down | QSYS | QDIST |  |  | Functional | Operational | High | Test | Temperature condition: 50K | 3.2.3 Transient operational scenarios | RTM-06 |  | Active | Required for proper system functionality | 50 K threshold
RTM-011 | The QPLANT shall facilitate the warm-up of the cryogenic users from 2 K to 300 K in less than 5 days | The QPLANT shall facilitate the warm-up of the cryogenic users from 2 K to 300 K in less than 5 days | QSYS | QPLANT | WCS |  | Functional | Operational | High | Test | Temperature condition: 2K; Temperature condition: 300K; Value shall meet 5 | 3.2.3 Transient operational scenarios | RTM-06 |  | Active | Required for proper system functionality | 5 days maximum
RTM-012 | The QPLANT shall support the transition shown in Figure 6 for the warming-up of the cryogenic users, whether passively or actively (with QCELL heaters if available) | The QPLANT shall support the transition shown in Figure 6 for the warming-up of the cryogenic users, whether passively or actively (with QCELL heaters if available) | QSYS | QCELL |  |  | Functional | Operational | High | Test | Value shall meet 6 | 3.2.3 Transient operational scenarios | RTM-06 |  | Active | Required for proper system functionality | Multiple warming transitions
RTM-013 | The Contractor may implement a manual purging, manual conditioning, and manual initial preparation of the QPLANT | The Contractor may implement a manual purging, manual conditioning, and manual initial preparation of the QPLANT | QSYS | QPLANT | WCS |  | Functional | Operational | Medium | Test | Compliance with requirement as specified | 3.2.4 Other operational scenarios |  | RTM-014, RTM-015, RTM-016 | Active | Required for proper system functionality | Manual operation allowed
RTM-014 | The QPLANT shall adhere to the purge-parameter table (pressure, flow-rate, duration, allowable residual O₂) provided by SCK CEN during contract execution | The QPLANT shall adhere to the purge-parameter table (pressure, flow-rate, duration, allowable residual O₂) provided by SCK CEN during contract execution | QSYS | QPLANT | WCS |  | Performance | Safety | High | Test | Compliance with requirement as specified | 3.2.4 Other operational scenarios | RTM-013 |  | Active | Required for safe operation of cryogenic system | Per SCK CEN parameters
RTM-015 | The QPLANT shall facilitate an average retention rate of 0.8 g/s LHe per individual QCELL (24 g/s total) during the filling process | The QPLANT shall facilitate an average retention rate of 0.8 g/s LHe per individual QCELL (24 g/s total) during the filling process | QSYS | QCELL |  |  | Performance | Performance | High | Test | Value shall meet 0.8 g; Value shall meet 24 g | 3.2.4 Other operational scenarios | RTM-013 |  | Active | Required for proper system functionality | 0.8 g/s per QCELL, 24 g/s total
RTM-016 | During LHe filling, the QPLANT shall provide 2,900 L of LHe to the users | During LHe filling, the QPLANT shall provide 2,900 L of LHe to the users | QSYS | QPLANT | WCS |  | Functional | Performance | High | Test | Value shall meet 2 ; Value shall meet 900 | 3.2.4 Other operational scenarios | RTM-013 |  | Active | Required for proper system functionality | 2,900 L LHe

## SBS
SBS ID | Name | Level | Parent | Children | Description
QSYS | Cryogenic System | 0 |  | QSYS-PR | Complete cryogenic system including plant, infrastructure, and distribution
QSYS-PR | Project Requirements | 0 |  | QPLANT, QINFRA, QCELL, QDIST | Overall project requirements and constraints
QPLANT | Cryoplant | 1 | QSYS-PR | WCS, QRB | Main cryogenic refrigeration plant including compressors and cold box
QINFRA | Cryogenic Infrastructure | 1 | QSYS-PR | WCS, QRB | CSS cryogenic supply system infrastructure
QCELL | Cryogenic Cell | 1 | QSYS-PR |  | CSS cryogenic USER - individual cryomodule and valve box combinations
QDIST | Cryogenic Distribution | 1 | QSYS-PR |  | CSS cryogenic USER - distribution lines and headers
WCS | Warm Compressor Station | 2 | QPLANT | PVPS, HP | Warm compression system including LP to HP and VLP to LP compressors
QRB | Refrigeration Cold Box | 2 | QPLANT | CC, TURBINES, BATH-4K, BATH-2K | Cold box containing refrigeration equipment and heat exchangers
PVPS | Pressure Vessel & Piping System | 3 | WCS |  | Pressure vessels, piping, and associated safety systems for WCS
HP | High Pressure System | 3 | WCS |  | High pressure compressors and associated equipment
CC | Cold Compressors | 3 | QRB |  | Cold compression equipment within refrigeration cold box
TURBINES | Turbo Expanders | 3 | QRB |  | Turbine expanders for refrigeration cycle
BATH-4K | 4K Bath System | 3 | QRB |  | 4K temperature helium bath and associated equipment
BATH-2K | 2K Bath System | 3 | QRB |  | 2K temperature helium bath and associated equipment

## Summary
Metric | Count
Total Requirements | 16
High Priority Requirements | 15
Medium Priority Requirements | 1
Safety Requirements | 0
Performance Requirements | 4
Functional Requirements | 11
Design Requirements | 1
Interface Requirements | 0
Requirements Needing Test Verification | 15
Requirements Needing Analysis Verification | 0
Requirements Needing Demonstration | 1
Operational Requirements | 10
Maintenance Requirements | 1
Lifetime Requirements | 1

## BySystem
SBS Level 1 | Design | Functional | Performance
QCELL | 0 | 3 | 1
QDIST | 0 | 1 | 0
QPLANT | 1 | 7 | 3

## ByType
Category | Design | Functional | Performance
Lifetime | 1 | 0 | 0
Maintenance | 0 | 1 | 0
Operational | 0 | 9 | 1
Performance | 0 | 1 | 2
Safety | 0 | 0 | 1