SCK CEN Ref.:	SCK CEN/ xxx xxxx

Third Party Ref.:

QPLANT - Granting Phase

HVAC Ducting & HP Compressor Exhaust

Tender reference: 2024-XXX-AF

SBS level: MINERVA-ATS-QSYST-QPLANT-WCS

Table of Contents

1	System Overview	2

1.1	Objective	2

1.2	Data Sources	2

2	Compressor Cooling Air & Exhaust Interface Specifications	2

2.1	Compressor Parameters	2

2.2	Total Compressor Parameters	2

3	Duct Sizing & Exhaust Design Calculations	2

3.1	Calculation for Individual and Full-System Exhaust Ducting	2

3.1.1	Single Compressor Duct Sizing	3

3.1.2	Full Installation (4 Compressors) Duct Sizing	3

3.2	Transition from Compressor Exhaust to Main Ducting	3

3.3	Estimated Pressure Drop for Transition	3

4	HVAC Integration Impact – Compressor Model Comparison	3

4.1	HVAC Integration Impact – Compressor Model Comparison	3

4.2	HVAC Summary Table (Updated for Ambient Heat Load Distribution & Pressure Drop)	4

5	Conclusion	4

# System Overview

## Objective

Design an optimized exhaust ducting and air-flow interface for helium compressor installations, ensuring:

- Nominal Compressed Helium Flow: ~350 g/s (four-unit FSD-based system or two-unit HSD-based combi system).

- Exhaust Air Handling: Proper removal of "direct air cooling" loads (~55-60 kW) via a duct system with minimal pressure drop, maintaining exhaust air T_max: +25°C to +40°C.

- Interface & Utilities: Integration with electrical (variable frequency drives), cooling water circuits, and HVAC (ambient heat removal and energy recovery).

## Data Sources

Below is the formal reference table listing all documents along with their corresponding SCK CEN codes. This table is prepared in accordance with contractual documentation standards and is intended for use in technical reference and traceability purposes.

| No. | Document Title | Description | SCK CEN Code |
| --- | --- | --- | --- |
| 1 | ALaT.pdf | Compressor Datasheet | SCK CEN/91177006 |
| 2 | KAEZER_Compressor Catelogue.pdf | Compressor Catalogue | SCK CEN/91174242 |
| 3 | KAEZER_General Assembly.pdf | General Assembly | SCK CEN/91176783 |
| 4 | Kaezer_Ventilation.pdf | Ventilation System | SCK CEN/91177009 |
| 5 | Keazer_Compressor Installation Guide.pdf | Compressor Installation Guide | SCK CEN/91174241 |
| 6 | LINDE.pdf | Compressor Datasheet | SCK CEN/91177005 |
| 7 | 01. Linde KT industrial pre-study cryoplant | Industrial Pre-study Cryoplant | SCK CEN/50173715 |
| 8 | 03. AL-aT industrial pre-study cryoplant | Industrial Pre-study Cryoplant | SCK CEN/50174360 |

# Compressor Cooling Air & Exhaust Interface Specifications

## Compressor Parameters

2 Compressor Cooling Air & Exhaust Interface Specifications

2.1 Compressor Parameters

| Compressor Model | Helium Flow (g/s) | Electrical Power (kW) | Cooling Water Load (kW) | Direct Air-Cooling Load (kW) | HVAC (Ambient Heat) (kW) |
| --- | --- | --- | --- | --- | --- |
| FSD 475 | 87.5 | 300 | 264 | 14.6 | 12.8 |
| FSD 575 | 87.5 | 271 | 253 | 13.6 | 11.7 |
| HSD Combi | 175 | 600 | 570 | 29.0 | 23.0 |

## Total Compressor Parameters

| Parameter | Total Value |
| --- | --- |
| Total Helium Flow (g/s) | 350.0 |
| Total Electrical Power (kW) | 1171 |
| Total Cooling Water Load (kW) | 1087 |
| Total Direct Air-Cooling Load (kW) | 57.2 |
| Total HVAC (Ambient Heat) (kW) | 47.5 |

# Duct Sizing & Exhaust Design Calculations

## Calculation for Individual and Full-System Exhaust Ducting

Assumptions:

- Direct Air-Cooling Load (Q):		 58 kW

- Specific Heat Capacity (cₚ): 		~1.005 kJ/(kg·K)

- Assumed Air Temperature Rise (∆T): 	10 K

- Air Density (ρ): 				1.2 kg/m³

- Design Air Velocity (v): 			5 m/s

### Single Compressor Duct Sizing

| Parameter | Formula | Calculation | Result |
| --- | --- | --- | --- |
| Mass Flow Rate (Ṁ) | Qcₚ⋅∆T | 581.005×10 | ~5.77 kg/s |
| Volumetric Flow Rate (V̇) | Ṁρ | 5.771.2 | ~4.81 m³/s |
| Required Duct Cross-Section (A) | Vv | 4.815 | ~0.96 m² |
| Equivalent Circular Duct Diameter | 4Aπ | 4×0.96π | ~1.1 m |
| Equivalent Square Duct Dimensions | AA | 0.96 | ~0.98 m × 0.98 m |

### Full Installation (4 Compressors) Duct Sizing

| Parameter | Formula | Calculation | Result |
| --- | --- | --- | --- |
| Total Mass Flow Rate | 4 ×Ṁ | 4×5.77 | ~23.08 kg/s |
| Total Volumetric Flow Rate | 4×V | 4×4.81 | ~19.24 m³/s |
| Required Duct Cross-Section (A) | Vv | 19.245 | ~3.85 m² |
| Equivalent Circular Duct Diameter | 4Aπ | 4×3.85π | ~2.21 m |
| Equivalent Square Duct Dimensions | AA | 3.85 | ~1.96 m × 1.96 m |

## Transition from Compressor Exhaust to Main Ducting

| Configuration | Transition Design |
| --- | --- |
| Single Compressor | 522 mm × 547 mm → 1.1 m circular or 1.0 × 1.0 m rectangular duct |
| Two Compressor Manifold | Two 1.1 m ducts → 1.8 m circular or 1.5 × 1.5 m rectangular manifold |
| Four Compressor System | Four 1.1 m ducts → 2.21 m circular or 1.96 × 1.96 m rectangular manifold |

## Estimated Pressure Drop for Transition

| System Configuration | Estimated Pressure Drop (∆P) |
| --- | --- |
| Single Compressor Exhaust | ~8.18 Pa |
| Two Compressor Manifold | ~12.5 Pa |
| Four Compressor System | ~19.3 Pa |

Target: Maintain total pressure drop within 50-100 Pa.

# HVAC Integration Impact – Compressor Model Comparison

## HVAC Integration Impact – Compressor Model Comparison

| Configuration | Electrical Power (kW) | Cooling Water Load (kW) | Direct Air-Cooling Load (kW) | HVAC (Ambient Heat) (kW) |
| --- | --- | --- | --- | --- |
| FSD 475 (4 Units) | 1203 | 1057 | 58 (design value) | 51 |
| FSD 575 (4 Units) | 1084 | 1011 | 54.4 | 46.7 |
| HSD (2 Combi Unit) | 1200 | 1140 | 58 | 46 |

## HVAC Summary Table (Updated for Ambient Heat Load Distribution & Pressure Drop)

| Configuration | Cooling Air Flow (m³/h) | Exhaust Dimensions (mm) | Total HVAC (Ambient Heat) Load per System (kW) | Estimated Pressure Drop (ΔP) (Pa) |
| --- | --- | --- | --- | --- |
| Single Compressor (FSD 475/575) | ~40,000 | 522 mm × 547 mm → 1.1 m circular | 58 kW | ΔP = 8.18 Pa |
| Two Compressors (Manifold) | ~80,000 | 1.8 m circular or 1.5 × 1.5 m square | 29 kW per compressor (Total: 58 kW) | ΔP = 12.5 Pa |
| Four Compressor System | ~160,000 | 2.21 m circular or 1.96 × 1.96 m square | 14.5 kW per compressor (Total: 58 kW) | ΔP = 19.3 Pa |

Note: HVAC Summary Table (4.2), reflect only the HVAC to ambient and not the full load

# Conclusion

It is hereby determined that QPLANT shall be configured with either:

- Four (4) units of the FSD 475/575 compressors (or an equivalent alternative), OR

- Two (2) HSD 800 series units (each incorporating two (2) compressors per skid).

The precise installation location remains under evaluation but is designated along the east wall of the WCS room in the CCB to minimize electrical cabling length.

Additionally, penetration design—whether:

- As single-unit exhaust,

- As a manifold configuration, OR

- As part of HV02 full HVAC load discharge (either ambient or cooling air).

Shall be executed under ACC NF responsibility to ensure full compliance with overall system design and operational objectives.

This design flow is irrespective of ‘nominal’ operation of Electrical input and cooling which represent a 350 g/s flow via combined compressor HP flow. Electrical Design is 353 kW per HP compressor, FSD 575 used as enveloping reference

This design flow is irrespective of ‘nominal’ operation of Electrical input and cooling which represent a 350 g/s flow via combined compressor HP flow. Electrical Design is 353 kW per HP compressor, FSD 575 used as enveloping reference