SCK CEN Ref.:	SCK CEN/ xxx xxxx

Third Party Ref.:

QPLANT - Granting Phase

Interface QPLANT | ACC NF (support systems)

Physical, Signal, Control & Nnterlock

Tender reference: 2024-XXX-AF

SBS level: MINERVA-ATS-QSYST-QPLANT-WCS

Author: Gerkotze Bonthuys (ATS/ACR – Process Engineering Discipline)

author bias: QPLANT_Owner (QPLANT Process Expert, Design Expert, Operator, Technician)

Table of Contents

1	Introduction terminal points and interfaces: QPLANT | ACC NF	- 3 -

1.1	Types of interaction	- 3 -

1.2	Numbered List of Support Systems and Their Terminal Points	- 3 -

1.3	Simple Interface diagram	- 4 -

1.3.1	Physical	- 4 -

1.3.2	Signal	- 4 -

2	Quantified Interface List (Detailed Terminal Points)	6

2.1	Detail Terminal Points	6

3	Singnal (I/O) Interface List (Expected Signals)	8

3.1	Specific Signals and sensors	10

3.2	PS01 Cooling Water System	10

3.3	HV02 HVAC Exhaust System	10

3.4	HV04 General HVAC (Room Environment)	10

3.5	HV06 HVAC Heating (40/50°C)	10

3.6	ES02 Electrical System	11

3.7	Specific Control System Detail – Granularity – See APPENDIX I	11

3.8	Control & Interlock Terminal Points (Optional/Additional)	11

3.9	Signal summary –	11

3.10	Control and Signal (summary)	13

APPENDIX – Additional Granular Detail	14

Electrical ES02 – Expanded singals	14

# PS05 Instrument Air & Nitrogen	15

# HV02 HVAC/Exhaust	15

# HV06 Heat Recuperation	15

# ES02 Electrical	15

# QPLANT IACS Aggregation	15

Table of Tables

Table 1 Detail Terminal Points	6

Table 2 Quantified Interface List (Expected Signals) – numbers are hypothetical (actual number in the respective support system total BASIC design File – (P&ID, Sizing Note, Detailed Description) – Globally (all support systems) have a combined: SSC list (structures system and components – this is SBS up to full Line Replacable items – and tag numbers – E.g. Tempeature sensor on the return line of	8

Table 3 PS01 Cooling Water System	10

Table 4 HV02 HVAC Exhaust System	10

Table 5 HV04 General HVAC (Room Environment)	10

Table 6 HV06 HVAC Heating (40/50°C)	10

Table 7 ES02 Electrical System	11

Table 8 Control & Interlock Terminal Points (Optional/Additional)	11

Table 9 Signal summary	12

Table 10 Control and Signal (summary)	13

Table 11 Electrical Terminal Points – Detailed Table	14

# Introduction terminal points and interfaces: QPLANT | ACC NF

## Types of interaction

Inputs to QPLANT:
Data signals from PS01, PS05, HV03 (CCB) HV06, and ES02 such as temperatures, pressures, flow rates, and electrical parameters. Alarm signals, interlock statuses, and diagnostic data are aggregated via UBMS (for soft interlocks/alarms) and BEPS (for hardwired safety interlocks).

Outputs from QPLANT:
Control commands and setpoints (e.g., pump start/stop, valve adjustments, fan speed, emergency shutdown signals) are sent out to the support systems. Both QPLANT TP1 and TP2 channels can handle these bidirectional communications.

Terminal Points (TPs):
These are defined to capture both main supply feeds (main TPs) and the control/instrumentation (control TPs). In this proposal, the primary QPLANT interfaces (TP1/TP2) are used as central aggregation points

## Numbered List of Support Systems and Their Terminal Points

- Process Systems (Cooling & Instrument Air)

  - PS01 – Cooling Water Supply & Return:
Supplies cooling water to the compressor room; return lines provide process cooling feedback.

  - PS05 – Instrument Air & Nitrogen Supply:
Provides instrument air for valve actuation and nitrogen for absorber regeneration.

- HVAC Systems

  - HV03– HVAC for Compressor Exhaust & Room Load (CCB – WCS)
Manages room air, exhaust flow, and temperature control in the compressor room.

  - HV06 – Heat Recuperation:
Provides a 40–50°C water supply/return loop for heat recovery from the process.

  - HV02 – QRB (AUB):
(Optional/Additional) Specialized ventilation for the cold box.

- Electrical Systems (ES02 – Low Voltage, up to 400 V)

  - Electrical Feeds for HPC:
Main electrical feeds for HP compressors (HP1–HP4) including VFD control.

  - UPS Backup and Additional Feeds:
Provides UPS backup for control systems, feeds for cold compressors, and other auxiliary electrical loads.

- ACC NF Terminal Points

  - These represent the connection points where the ACC NF system integrates with QPLANT and the above support systems.

- QPLANT I/O Interface Grouping

  - Inputs (TP1): # (TP1 is requestor of service – check if TP1 also = to INPUT – think not)
Signals requested by QPLANT from the support systems (process measurements, alarms, diagnostic data).

  - Outputs (TP2):
Commands and setpoints sent from QPLANT to support systems (control signals, interlocks).

## Simple Interface diagram

### Physical

MINERVA (ACC NF)

├── PS01 Cooling Water

│   ├── TP-PS01-001 (Supply CCB)

│   └── TP-PS01-002 (Return CCB)

├── HV03 HVAC Exhaust for 4 X HP compressors (CCB) x 4 TP into single exhaust or multiple exitst the roof
├── HV02 HVAC Exhaust (TBD – there is possible safety line (PSV or BD) exhaust (or additional overpressure protection that need safe (‘***AND OUTSIDE***’) venting to avoid operator asphyxiation or cold burn – safe evac (roof penetration – NA.BA + NA.CE

│   └── TP-HV02-001 (Main Exhaust Duct)

├── HV06 HVAC Heating

│   └── TP-HV06-001 (Supply/Return lines) – ONLY for heat integration? The room does need heating? Maybe

├── ES02 Electrical

│   ├── TP-ES02-001 (CCB Power Feed)

│   └── TP-ES02-002 (QRB Power Feed)

└── PS05 Industrial Gases

├── TP-PS05-001 (Instr. Air CCB)
├── TP-PS05-001 (Instr. Air QRB)

└── TP-PS05-003 (Nitrogen CCB)
└── TP-PS05-004 (Nitrogen QRB)
└── TP-PS05-005 (Nitrogen QRB)Speciality gases (helium 5.0 and Helium 6.0, nitrogen argon, oxygen, - single cylinders – exclude welding gas (this deemed separate in execution than QPLANT responsigiblbgh

### Signal

MINERVA, UBMS (this is available signals from the support systems – all signal information to QPLANT via MCS (even hardwired interlocks – e.g.: minimum flow switch in the main cooling water (heat sink from ACC NF: PAB12 (Adiabatic cooling – 27°C fixed supply)

Thus event (LOF Loss of flow (or reducing and overcoming a threshold to the enveloping LOCA (loss of cooling and coolant accident – A ‘dry pipe’ with heat source not switched off.

If PAB12 return FLOW switch is triggered, PAB12 Hardwired signal (UEPS) UEPS PLC – HARDWIRED to MCS (primary system) – they trigger interlock with QPLANT – NO direct coms.

The contractor is free to suggest or proposes specific signals of interazte (NOT control – only moniot) – as well as expected interlocks (!!!! Bi-directional) 

If QPLANT(and per def QPALNT:CS) triggers an interlock event (Cold Compressor Trip cannot sustain 2K Operation – Heat source (RF load – which is 2K dynamic heat load) needs to be removed (or cut) – This is done on a per QCELL (modular) as well as orcherstated (MCS QCELL broker) to facilate inforamiton share – Infoshare is just that – NON critgical -non safety rated – if it is rehte gereza, if vcall away -we cn manage , but please return qukcly since we run betr togger – thus expecting smaller operating windows and different response (in time as well as action) form QPLANT (QRB and WCS). This shall be a joined effort with process design (mirror lifechylez of QPLANT) and involve SCK CEN stakeodlez for validation (are we building the rign thing) – Continuous control develipoe post Detailed design? Applicaq to indicat acti gaaan expected output

├── Signals, Sensors, Alarms

│   ├── PS01 Cooling Water

│   ├── HV02 HVAC Exhaust

│   ├── HV04 General HVAC

│   ├── HV06 HVAC Heating (40/50°C)

│   └── ES02 Electrical System

# Quantified Interface List (Detailed Terminal Points)

This table lists the key terminal points, including the expected parameter values (e.g., pressure, temperature, flow, voltage, power), the subsystem they belong to, the building and room location, and additional notes for each interface.

## Detail Terminal Points

Table 1 Detail Terminal Points

| TP ID | Interface Description | Subsystem | Building | Room | Discipline | Key Parameter(s) | Expected Value(s) | Additional Notes |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| PS01 – Cooling Water |  |  |  |  |  |  |  |  |
| TP.PS01:8001 | Cooling Water Supply | PS01 | CCB | Compressor Room | Process | Temperature, Pressure, Flow Rate | Temp: ~27°C; Pressure: 1–3 barg | Main supply header from ACC NF; glycol water mix |
| TP.PS01:8002 | Cooling Water Return | PS01 | CCB | Compressor Room | Process | Temperature, Pressure, Flow Rate | Temp: ~35°C; Pressure: similar range | Main return header |
| PS05 – Instrument Air & Nitrogen |  |  |  |  |  |  |  |  |
| TP.PS05:8003 | Instrument Air Supply (WCS side) | PS05 | CCB | Compressor Room | Process | Pressure, Flow Rate | Pressure: ~8 bar | Supply for valve actuation |
| TP.PS05:8004 | Instrument Air Supply (QRB side) | PS05 | AUB | Cold Box | Process | Pressure, Flow Rate | Pressure: ~8 bar | Local supply (backup) |
| TP.PS05:8005 | Nitrogen Supply (WCS side) | PS05 | CCB | Compressor Room | Process | Pressure | Pressure: ~7–8 bar | For absorber regeneration |
| TP.PS05:8006 | Nitrogen Supply (QRB side) | PS05 | AUB | Cold Box | Process | Pressure | Pressure: ~7–8 bar | Local nitrogen feed |
| HVAC – HV02 (Exhaust) & HV06 (Heat Recuperation) |  |  |  |  |  |  |  |  |
| TP.HV02:8007 | Compressor Exhaust | HV02 | CCB | Compressor Room | HVAC | Exhaust Flow, Pressure | Flow: ~4000 m³/h; Pressure: <40 Pa | Exhaust from HP compressors |
| TP.HV02:8008 | Exhaust Outlet / Bypass | HV02 | CCB | Compressor Room | HVAC | Airflow | High airflow | Vents exhaust to atmosphere or bypass |
| TP.HV06:8009 | Heat Recuperation Supply | HV06 | CCB | Heat Exchanger Rm | HVAC | Water Temperature, Flow Rate | Supply Temp: 40–50°C; Moderate flow | Supplies heat recovery loop (to QP.WCS.HPC); Pump rating ~4 kW |
| TP.HV06:8010 | Heat Recuperation Return | HV06 | CCB | Heat Exchanger Rm | HVAC | Water Temperature, Flow Rate | Temperature rise: 5–10°C above supply | Returns water from process heat sink; Pump rating ~4 kW |
| ES02 – Electrical |  |  |  |  |  |  |  |  |
| TP.ES02:8011 | Electrical Feed for HPC1 | ES02 | CCB | Electrical Room | Electrical | Voltage, Power | ~400 V AC; ~356 kW | Motor VFD for HP1 |
| TP.ES02:8012 | Electrical Feed for HPC2 | ES02 | CCB | Electrical Room | Electrical | Voltage, Power | ~400 V AC; ~356 kW | Motor VFD for HP2 |
| TP.ES02:8013 | Electrical Feed for HPC3 | ES02 | CCB | Electrical Room | Electrical | Voltage, Power | ~400 V AC; ~356 kW | Motor VFD for HP3 |
| TP.ES02:8014 | Electrical Feed for HPC4 | ES02 | CCB | Electrical Room | Electrical | Voltage, Power | ~400 V AC; ~356 kW | Motor VFD for HP4 |
| TP.ES02:8015 | Electrical UPS Backup | ES02 | CCB | Electrical Room | Electrical | Runtime, Voltage | 15–30 min backup | UPS for control system backup |
| TP.ES02:8016 | Electrical Feed for Cold Compressor 1 | ES02 | AUB | Cold Box | Electrical | Voltage, Power | ~400 V AC; ~28 kW | Supply for Cold Compressor 1 |
| TP.ES02:8017 | Electrical Feed for Cold Compressor 2 | ES02 | AUB | Cold Box | Electrical | Voltage, Power | ~400 V AC; ~28 kW | Supply for Cold Compressor 2 |
| TP.ES02:8018 | Electrical Feed for Cold Compressor 3 | ES02 | AUB | Cold Box | Electrical | Voltage, Power | ~400 V AC; ~28 kW | Supply for Cold Compressor 3 |
| TP.ES02:8019 | Electrical Feeder for Other Supplies | ES02 | AUB | Cold Box | Electrical | Voltage, Power | ~400 V AC; ~43 kW | Feeder for auxiliary loads |
| QPLANT IACS Aggregation |  |  |  |  |  |  |  |  |
| TP.QPLANT:9001 | QPLANT Input Aggregation | QPLANT | Central | Control Room | IACS | Data, Alarms, Diagnostics | Real-time | Aggregates inputs from PS01, PS05, HV02, HV06, ES02 |
| TP.QPLANT:9002 | QPLANT Output Aggregation | QPLANT | Central | Control Room | IACS | Setpoints, Commands | Real-time | Sends control commands to support systems |

# Singnal (I/O) Interface List (Expected Signals)

Table 2 Quantified Interface List (Expected Signals) – numbers are hypothetical (actual number in the respective support system total BASIC design File – (P&ID, Sizing Note, Detailed Description) – Globally (all support systems) have a combined:
SSC list (structures system and components – this is SBS up to full Line Replacable items – and tag numbers – E.g. Tempeature sensor on the return line of

| TP ID | Interface Description | Subsystem | Building | Room | Discipline | Key Parameter(s) | Expected Value(s) | Additional Notes |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| PS01 – Cooling |  |  |  |  |  |  |  |  |
| TP.PS01:8001 | Cooling Water Supply | PS01 | CCB | Compressor Room | Process | Temperature, Pressure, Flow Rate | Temp: ~27°C, Pressure: 1–3 barg | Main supply header from ACC NF; Glycol water mix |
| TP.PS01:8002 | Cooling Water Return | PS01 | CCB | Compressor Room | Process | Temperature, Pressure, Flow Rate | Temp: ~35°C, Pressure: similar range | Main return header to ACC NF or process loop |
| PS05 – Instrument Air & Nitrogen |  |  |  |  |  |  |  |  |
| TP.PS05:8003 | Instrument Air Supply (WCS side) | PS05 | CCB | Compressor Room | Process | Pressure, Flow Rate | Pressure: ~8 bar | Supply for valve actuation (WCS feed) |
| TP.PS05:8004 | Instrument Air Supply (QRB side) | PS05 | AUB | Cold Box | Process | Pressure, Flow Rate | Pressure: ~8 bar | Local supply from QRB backup |
| TP.PS05:8005 | Nitrogen Supply (WCS side) | PS05 | CCB | Compressor Room | Process | Pressure | Pressure: ~7–8 bar | For absorber regeneration |
| TP.PS05:8006 | Nitrogen Supply (QRB side) | PS05 | AUB | Cold Box | Process | Pressure | Pressure: ~7–8 bar | Local nitrogen feed |
| HVAC – Exhaust & Heat Recuperation |  |  |  |  |  |  |  |  |
| TP.HV02:8007 | Compressor Exhaust | HV02 | CCB | Compressor Room | HVAC | Exhaust Temperature, Flow Rate, pressure drop | Flow: ~4000 m³/h, <40 Pa Exhaust (terminal point) ‘squaure’ or circule conneciotn deisgn | Exhaust from HP compressors |
| TP.HV02:8008 | Exhaust Outlet / Bypass | HV02 | CCB | Compressor Room | HVAC | Airflow | High airflow | Direct venting or bypass outlet |
| TP.HV06:8009 | Heat Recuperation Supply | HV06 | CCB | Heat Exchanger Room | HVAC | Water Temperature, Flow Rate | 40–50°C supply, moderate flow | Supplies heat recovery loop (to QP.WCS.HPC) |
| TP.HV06:8010 | Heat Recuperation Return | HV06 | CCB | Heat Exchanger Room | HVAC | Water Temperature, Flow Rate. Heat SINK NEED or balance (is there a place for this? | 5–10°C rise above supply | Returns water from process heat sink |
| ES02 – Electrical Feeds |  |  |  |  |  |  |  |  |
| TP.ES02:8011 | Electrical Feed for HPC1 | ES02 | CCB | Electrical Room | Electrical | Voltage, Power | ~400 V AC, ~356 kW | Primary feed for HP Compressor 1 (Motor VFD) |
| TP.ES02:8012 | Electrical Feed for HPC2 | ES02 | CCB | Electrical Room | Electrical | Voltage, Power | ~400 V AC, ~356 kW | Primary feed for HP Compressor 2 |
| TP.ES02:8013 | Electrical Feed for HPC3 | ES02 | CCB | Electrical Room | Electrical | Voltage, Power | ~400 V AC, ~356 kW | Primary feed for HP Compressor 3 |
| TP.ES02:8014 | Electrical Feed for HPC4 | ES02 | CCB | Electrical Room | Electrical | Voltage, Power | ~400 V AC, ~356 kW | Primary feed for HP Compressor 4 |
| TP.ES02:8015 | Electrical UPS Backup | ES02 | CCB | Electrical Room | Electrical | Runtime, Voltage | 15–30 min backup | UPS for control system backup |
| TP.ES02:8016 | Electrical Feed for Cold Compressor 1 | ES02 | AUB | Cold Box | Electrical | Voltage, Power | ~400 V AC, ~28 kW | Supply for Cold Compressor 1 |
| TP.ES02:8017 | Electrical Feed for Cold Compressor 2 | ES02 | AUB | Cold Box | Electrical | Voltage, Power | ~400 V AC, ~28 kW | Supply for Cold Compressor 2 |
| TP.ES02:8018 | Electrical Feed for Cold Compressor 3 | ES02 | AUB | Cold Box | Electrical | Voltage, Power | ~400 V AC, ~28 kW | Supply for Cold Compressor 3 |
| TP.ES02:8019 | Electrical Feeder for Other Supplies | ES02 | AUB | Cold Box | Electrical | Voltage, Power | ~400 V AC, ~43 kW | Feeder for auxiliary loads |
| QPLANT IACS – Aggregation |  |  |  |  |  |  |  |  |
| TP.QPLANT:9001 | QPLANT Input Aggregation | QPLANT | Central | Control Room | IACS | Data, Alarm, Status | Real-time | Aggregates inputs from PS01, PS05, HV02, HV06, ES02 |
| TP.QPLANT:9002 | QPLANT Output Aggregation | QPLANT | Central | Control Room | IACS | Setpoints, Commands | Real-time | Sends control commands to support systems |

## Specific Signals and sensors

- QPLANT = TP1

- Support Systems (via MCS to QPLANT:CS) = TP2

## PS01 Cooling Water System

Table 3 PS01 Cooling Water System

| TP ID | Type | Description | Location | Parameters |
| --- | --- | --- | --- | --- |
| PS01-001 | Sensor | Supply Temperature Sensor | CCB Compressor Rm | Temperature |
| PS01-002 | Sensor | Return Temperature Sensor | CCB Compressor Rm | Temperature |
| PS01-003 | Sensor | Supply Pressure Sensor | CCB Compressor Rm | Pressure |
| PS01-004 | Sensor | Return Flow Rate Sensor | CCB Compressor Rm | Flow rate |
| PS01-005 | Alarm | Low Flow Alarm | CCB Compressor Rm | Flow Threshold |
| PS01-006 | Alarm | High Temperature Alarm | CCB Compressor Rm | Temperature Threshold |

## HV02 HVAC Exhaust System

Table 4 HV02 HVAC Exhaust System

| TP ID | Type | Description | Location | Parameters |
| --- | --- | --- | --- | --- |
| HV02-001 | Sensor | Exhaust Airflow Sensor | CCB Compressor Rm | Airflow |
| HV02-002 | Sensor | Exhaust Temperature Sensor | CCB Compressor Rm | Temperature |
| HV02-003 | Alarm | Exhaust Fan Failure Alarm | CCB Compressor Rm | Fan Status |
| HV02-004 | Sensor | Room Differential Pressure Sensor | CCB Compressor Rm | Pressure differential |
| HV02-005 | Alarm | High Exhaust Temperature Alarm | CCB Compressor Rm | Temperature Threshold |

## HV04 General HVAC (Room Environment)

Table 5 HV04 General HVAC (Room Environment)

| TP ID | Type | Description | Location | Parameters |
| --- | --- | --- | --- | --- |
| HV04-001 | Sensor | Room Temperature Sensor | CCB & QRB Rooms | Temperature |
| HV04-002 | Sensor | Room Humidity Sensor | CCB & QRB Rooms | Relative Humidity (%) |
| HV04-003 | Alarm | Room Temperature High Alarm | CCB & QRB Rooms | Temperature Threshold |
| HV04-004 | Alarm | Room Humidity High Alarm | CCB & QRB Rooms | Humidity Threshold |

## HV06 HVAC Heating (40/50°C)

Table 6 HV06 HVAC Heating (40/50°C)

| TP ID | Type | Description | Location | Parameters |
| --- | --- | --- | --- | --- |
| HV06-001 | Sensor | Supply Water Temperature Sensor (40°C) | CCB Compressor Rm | Temperature |
| HV06-002 | Sensor | Return Water Temperature Sensor (50°C) | CCB Compressor Rm | Temperature |
| HV06-003 | Alarm | Heating Loop Low Temperature Alarm | CCB Compressor Rm | Temperature Threshold |
| HV06-004 | Alarm | Heating Loop Flow Low Alarm | CCB Compressor Rm | Flow Threshold |

## ES02 Electrical System

Table 7 ES02 Electrical System

| TP ID | Type | Description | Location | Parameters |
| --- | --- | --- | --- | --- |
| ES02-001 | Sensor | MCC Main Feed Voltage/Current Sensor | CCB Compressor Rm | Voltage, Current |
| ES02-002 | Alarm | MCC Main Breaker Trip Alarm | CCB Compressor Rm | Breaker status |
| ES02-003 | Sensor | UPS Battery Health/Voltage Sensor | CCB Compressor Rm | Battery health |
| ES02-004 | Alarm | UPS Battery Fault Alarm | CCB Compressor Rm | Fault Status |
| ES02-005 | Sensor | Instrumentation DC Voltage Monitor (24V) | CCB & QRB Rooms | Voltage |
| ES02-006 | Alarm | Instrumentation Power Loss Alarm | CCB & QRB Rooms | Voltage Threshold |

## Specific Control System Detail – Granularity – See APPENDIX I

## Control & Interlock Terminal Points (Optional/Additional)

- These are not the main supply points but are instrumentation and control points attached to them

Table 8 Control & Interlock Terminal Points (Optional/Additional)

| TP ID | Interface | Subsystem System | Connection Support System | Building | Room | DataType | Notes |
| --- | --- | --- | --- | --- | --- | --- | --- |
| PS01:9001 | PS01 Supply Pressure Sensor | PS01 | Attached to PS01 Supply | CCB | Compressor Room | REAL | Monitors cooling water supply pressure |
| PS01:9002 | PS01 Return Temperature Sensor | PS01 | Attached to PS01 Return | CCB | Compressor Room | REAL | Monitors return water temperature |
| HV02:9003 | HV02 Exhaust Damper Actuator | HV02 | Attached to HV02 Exhaust | CCB | Compressor Room | BIT | Controls damper position for exhaust bypass |
| ES02:9004 | HPC1 Overload Relay | ES02 | Integrated with ES02 Feed for HPC1 | CCB | Electrical Room | BIT | Provides hardwired interlock for overload conditions |
| ES02:9005 | UPS Status Monitor | ES02 | Monitors UPS output | CCB | Electrical Room | NVARCHAR(255) | Monitors battery charge, runtime, fault conditions |

## Signal summary –

ATTENTION NFS Please give sensor name (tagname and number) as well as terminal point name (as per ACC NF TP list or

Signal summary –

Table 9 Signal summary

| TP ID | Description | Subsystem | Support System | Room | Notes |
| --- | --- | --- | --- | --- | --- |
| 8005 | Exhaust Flow Sensor | HV02 | HVAC | CCB Compressor Rm | Flow sensor |
| 8006 | Exhaust Temperature Sensor | HV02 | HVAC | CCB Compressor Rm | Temperature sensor |
| 8007 | Exhaust Damper Actuator | HV02 | HVAC | CCB Compressor Rm | Actuator, bypass control |
| 8008 | HVAC Room Airflow Monitor | HV02 | HVAC | CCB Compressor Rm | Room airflow monitoring |
| 8009 | HV06 Supply Temperature Sensor | HV06 | HVAC Heat Recup. | CCB Compressor Rm | Temperature sensor |
| 8010 | HV06 Flow Control Valve | HV06 | HVAC Heat Recup. | CCB Compressor Rm | Flow control |
| 8011 | HV06 Return Temperature Sensor | HV06 | HVAC Heat Recup. | CCB Compressor Rm | Return temp. monitoring |
| 8012 | HV06 Return Flow Rate Monitor | HV06 | HVAC Heat Recup. | CCB Compressor Rm | Return flow rate |
| 8013 | PS01 Supply Pressure Sensor | PS01 | Cooling | CCB Compressor Rm | Pressure sensor |
| 8014 | PS01 Flow Control Valve | PS01 | Cooling | CCB Compressor Rm | Supply flow control |
| 8015 | PS01 Return Temperature Sensor | PS01 | Cooling | CCB Compressor Rm | Return temp. monitoring |
| 8016 | PS01 Return Flow Rate Monitor | PS01 | Cooling | CCB Compressor Rm | Return flow monitoring |
| 8017 | PS05 Instr Air Flow Sensor (CCB) | PS05 | Instrument Air | CCB Compressor Rm | Flow monitoring |
| 8018 | PS05 Instr Air Pressure Regulator (CCB) | PS05 | Instrument Air | CCB Compressor Rm | Pressure regulation |
| 8019 | PS05 Instr Air Flow Sensor (QRB) | PS05 | Instrument Air | AUB Cold Box | Flow monitoring |
| 8020 | PS05 Instr Air Pressure Regulator (QRB) | PS05 | Instrument Air | AUB Cold Box | Pressure regulation |
| 8021 | PS05 Nitrogen Flow Sensor (CCB) | PS05 | Nitrogen | CCB Compressor Rm | Flow monitoring |
| 8022 | PS05 Nitrogen Pressure Regulator (CCB) | PS05 | Nitrogen | CCB Compressor Rm | Pressure regulation |
| 8023 | PS05 Nitrogen Flow Sensor (QRB) | PS05 | Nitrogen | AUB Cold Box | Flow monitoring |
| 8024 | PS05 Nitrogen Pressure Regulator (QRB) | PS05 | Nitrogen | AUB Cold Box | Pressure regulation |

## Control and Signal (summary)

Table 10 Control and Signal (summary)

| Signal ID | Description | System | Type | Location | Measurement/Control Function |
| --- | --- | --- | --- | --- | --- |
| CSP-001 | PS01 Supply Pressure Sensor | PS01 | Control | CCB Compressor Rm | Pressure sensing |
| CSP-002 | PS01 Return Temperature Sensor | PS01 | Control | CCB Compressor Rm | Temperature monitoring |
| CSP-003 | PS01 Flow Control Valve | PS01 | Control | CCB Compressor Rm | Flow regulation |
| CSP-004 | PS01 Return Flow Rate Monitor | PS01 | Signal | CCB Compressor Rm | Flow rate monitoring |
| CSP-005 | HV06 Supply Temperature Sensor | HV06 | Signal | CCB Compressor Rm | Temperature monitoring |
| CSP-006 | HV06 Return Temperature Sensor | HV06 | Signal | CCB Compressor Rm | Temperature monitoring |
| CSP-007 | HV06 Flow Control Valve | HV06 | Control | CCB Compressor Rm | Flow control |
| CSP-008 | HV06 Return Flow Rate Monitor | HV06 | Signal | CCB Compressor Rm | Flow rate monitoring |
| CSP-009 | HV02 Exhaust Flow Sensor | HV02 | Signal | CCB Compressor Rm | Exhaust flow measurement |
| CSP-010 | HV02 Exhaust Temperature Sensor | HV02 | Signal | CCB Compressor Rm | Exhaust temp measurement |
| CSP-011 | HV02 Exhaust Damper Actuator | HV02 | Control | CCB Compressor Rm | Exhaust flow/damper control |
| CSP-012 | HV02 HVAC Room Airflow Monitor | HV02 | Signal | CCB Compressor Rm | Room airflow monitoring |

# APPENDIX – Additional Granular Detail

## Electrical ES02 – Expanded/(#Anticipated?) Signals

Table 11 Electrical Terminal Points – Detailed Table

| Terminal Point ID | Description | Subsystem/ System | Connection/ Support System | Room | Parameters / Data Measured & Expected Values | Notes |
| --- | --- | --- | --- | --- | --- | --- |
| TP.8025 | ES02 Electrical Feed HP1 | ES02 | WCS (CCB) Electrical Feed | Electrical Room | Voltage, Current, Power Factor, Frequency, Harmonics, e.g., 400V AC, 50Hz, PF ≥ 0.9 | Main feed for HP1; monitors real-time power quality |
| TP.8026 | ES02 Electrical Feed HP2 | ES02 | WCS (CCB) Electrical Feed | Electrical Room | Voltage, Current, PF, Frequency; like TP.8025 | Main feed for HP2 |
| TP.8027 | ES02 Electrical Feed HP3 | ES02 | WCS (CCB) Electrical Feed | Electrical Room | Voltage, Current, PF, Frequency; similar ratings as TP.8025 | Main feed for HP3 |
| TP.8028 | ES02 Electrical Feed HP4 | ES02 | WCS (CCB) Electrical Feed | Electrical Room | Voltage, Current, PF, Frequency; similar ratings as TP.8025 | Main feed for HP4 |
| TP.8029 | ES02 Electrical UPS Backup | ES02 | UPS Backup for Control & Safety | Electrical Room | Battery Voltage, Charge/Discharge Status, Runtime (e.g., 15–30 minutes) | Ensures emergency loads during outages |
| TP.8030 | ES02 Electrical Transformer Input | ES02 | Transformer Input (HV to LV) | Electrical Room | Input Voltage, Current, Transformer Efficiency, Temperature, e.g., 11kV to 400V conversion, load ratings | Monitors HV to LV transformation performance |
| TP.8031 | ES02 Panel Supply to Control System | ES02 | Control System Panel Power | Electrical Room | Voltage stability, Current, Harmonic distortion; ±5% variation acceptable | Ensures stable power for control system panels |
| TP.8032 | ES02 Emergency Power Supply | ES02 | Emergency Backup Generator | Electrical Room | Output Voltage, Frequency, Power Capacity; 400V AC, 50Hz, rated for emergency load | Activated during grid failures |
| TP.8033 | ES02 Monitoring Sensor for Power Quality | ES02 | Power Quality Monitoring Interface | Electrical Room | Power Factor, Harmonics, Voltage Fluctuations, Frequency deviations | Detailed analysis to comply with IEC/IEEE standards |
| TP.8034 | ES02 Bus Bar Connection | ES02 | Bus Bar Connection | Electrical Room | Voltage Drop, Load Distribution, Connection Integrity | Monitors distribution efficiency at HV bus bar |
| TP.8035 | ES02 Load Balancing Sensor | ES02 | Load Balancing System | Electrical Room | Current distribution across phases; balanced within a few percent | Ensures equal load distribution across phases |
| TP.8036 | ES02 Redundant Electrical Feed | ES02 | Redundant Power Connection | Electrical Room | Status, Voltage, Current; minimal fluctuation in standby mode | Provides a backup feed in case of failure of main feed |

Utility detail (PS01, PS05, HV02 HV06, HV04) – Reliability lined support systems

# PS01 Cooling

TP_ID=TP.PS01:8001 INTERFACE="Cooling Water Supply" SYSTEM=PS01 BUILDING=CCB ROOM="Compressor Room" DATATYPE="NVARCHAR(255)" NOTES="Temp: ~27°C, Pressure: 1-3 barg; Main supply from ACC NF (glycol water)"

TP_ID=TP.PS01:8002 INTERFACE="Cooling Water Return" SYSTEM=PS01 BUILDING=CCB ROOM="Compressor Room" DATATYPE="NVARCHAR(255)" NOTES="Temp: ~35°C; Main return header"

# PS05 Instrument Air & Nitrogen

TP_ID=TP.PS05:8003 INTERFACE="Instrument Air Supply (WCS side)" SYSTEM=PS05 BUILDING=CCB ROOM="Compressor Room" DATATYPE="NVARCHAR(255)" NOTES="Pressure: ~8 bar; for valve actuation"

TP_ID=TP.PS05:8004 INTERFACE="Instrument Air Supply (QRB side)" SYSTEM=PS05 BUILDING=AUB ROOM="Cold Box" DATATYPE="NVARCHAR(255)" NOTES="Pressure: ~8 bar; local backup"

TP_ID=TP.PS05:8005 INTERFACE="Nitrogen Supply (WCS side)" SYSTEM=PS05 BUILDING=CCB ROOM="Compressor Room" DATATYPE="NVARCHAR(255)" NOTES="Pressure: ~7-8 bar; for regeneration"

TP_ID=TP.PS05:8006 INTERFACE="Nitrogen Supply (QRB side)" SYSTEM=PS05 BUILDING=AUB ROOM="Cold Box" DATATYPE="NVARCHAR(255)" NOTES="Pressure: ~7-8 bar; local feed"

# HV02 HVAC/Exhaust

TP_ID=TP.HV02:8007 INTERFACE="Compressor Exhaust" SYSTEM=HV02 BUILDING=CCB ROOM="Compressor Room" DATATYPE="NVARCHAR(255)" NOTES="4000 m³/h, <40 Pa; exhaust from HP compressors"

TP_ID=TP.HV02:8008 INTERFACE="Exhaust Outlet/Bypass" SYSTEM=HV02 BUILDING=CCB ROOM="Compressor Room" DATATYPE="NVARCHAR(255)" NOTES="High airflow; vents to atmosphere"

# HV06 Heat Recuperation

TP_ID=TP.HV06:8009 INTERFACE="Heat Supply" SYSTEM=HV06 BUILDING=CCB ROOM="Heat Exchanger Rm" DATATYPE=REAL NOTES="40-50°C supply; pump rating ~4 kW"

TP_ID=TP.HV06:8010 INTERFACE="Heat Return" SYSTEM=HV06 BUILDING=CCB ROOM="Heat Exchanger Rm" DATATYPE=REAL NOTES="Return with 5-10°C rise"

# ES02 Electrical

TP_ID=TP.ES02:8011 INTERFACE="Electrical Feed HPC1" SYSTEM=ES02 BUILDING=CCB ROOM="Electrical Room" DATATYPE="NVARCHAR(255)" NOTES="400 V AC, ~356 kW, Motor VFD"

TP_ID=TP.ES02:8012 INTERFACE="Electrical Feed HPC2" SYSTEM=ES02 BUILDING=CCB ROOM="Electrical Room" DATATYPE="NVARCHAR(255)" NOTES="400 V AC, ~356 kW, Motor VFD"

TP_ID=TP.ES02:8013 INTERFACE="Electrical Feed HPC3" SYSTEM=ES02 BUILDING=CCB ROOM="Electrical Room" DATATYPE="NVARCHAR(255)" NOTES="400 V AC, ~356 kW, Motor VFD"

TP_ID=TP.ES02:8014 INTERFACE="Electrical Feed HPC4" SYSTEM=ES02 BUILDING=CCB ROOM="Electrical Room" DATATYPE="NVARCHAR(255)" NOTES="400 V AC, ~356 kW, Motor VFD"

TP_ID=TP.ES02:8015 INTERFACE="UPS Backup" SYSTEM=ES02 BUILDING=CCB ROOM="Electrical Room" DATATYPE="NVARCHAR(255)" NOTES="15-30 min backup"

TP_ID=TP.ES02:8016 INTERFACE="Electrical Feed for ColdComp 1" SYSTEM=ES02 BUILDING=AUB ROOM="Cold Box" DATATYPE=REAL NOTES="400 V AC, ~28 kW"

TP_ID=TP.ES02:8017 INTERFACE="Electrical Feed for ColdComp 2" SYSTEM=ES02 BUILDING=AUB ROOM="Cold Box" DATATYPE=REAL NOTES="400 V AC, ~28 kW"

TP_ID=TP.ES02:8018 INTERFACE="Electrical Feed for ColdComp 3" SYSTEM=ES02 BUILDING=AUB ROOM="Cold Box" DATATYPE=REAL NOTES="400 V AC, ~28 kW"

TP_ID=TP.ES02:8019 INTERFACE="Electrical Feeder - Other Supplies" SYSTEM=ES02 BUILDING=AUB ROOM="Cold Box" DATATYPE=REAL NOTES="400 V AC, ~43 kW"

# QPLANT IACS Aggregation

TP_ID=TP.QPLANT:9001 INTERFACE="QPLANT Input Aggregation" SYSTEM=QPLANT BUILDING=Central ROOM="Control Room" DATATYPE="NVARCHAR(255)" NOTES="Aggregates inputs from PS01, PS05, HV02, HV06, ES02"

TP_ID=TP.QPLANT:9002 INTERFACE="QPLANT Output Aggregation" SYSTEM=QPLANT BUILDING=Central ROOM="Control Room" DATATYPE="NVARCHAR(255)" NOTES="Sends control commands to support systems"

# (TP2 is PROVIDERRS of service – check if TP1 also = to INPUT – think not)